## Summary Table
Turn off all excluding C & D grades
Row Labels | Count of CONDITION RANK | Average of Estimated Remaining Useful Design Life (YEARS) | Sum of Year 1 - 2018/19 | Sum of Year 2 - 2019/20 | Sum of Year 3 - 2020/21 | Sum of Year 4 - 2021/22 | Sum of Year 5 - 2022/23 | Sum of Total | Row Labels | Average of Likelihood Score (1-4) | Average of Consequence Score (1-5)
Protection Systems | [8 empty] | Ceiling Finishes
Fire Alarm Installations (inc, call points, sounders and detection) | [8 empty] | Mineral fibre suspended ceiling tiles 600 x 600
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Fire Alarm Installations (inc, call points, sounders and detection) Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Protection Systems Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Mineral fibre suspended ceiling tiles 600 x 600 Total | 2.6571 | 2
Ceiling Finishes | [8 empty] | Suspended Ceiling Tile - Metal
Mineral fibre suspended ceiling tiles 600 x 600 | [8 empty] | MODERATE | 3 | 2
B | 43 | 9.7674 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
C | 35 | 2.6286 | 0 | 19956.3759 | 15934.8186 | 0 | 0 | 35891.1945 | Suspended Ceiling Tile - Metal Total | 2.5 | 2
A | 5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Mineral fibre suspended ceiling tiles 600 x 1200
Mineral fibre suspended ceiling tiles 600 x 600 Total | 83 | 7.494 | 0 | 19956.3759 | 15934.8186 | 0 | 0 | 35891.1945 | MODERATE | 3 | 2
Suspended Ceiling Tile - Metal | [8 empty] | Mineral fibre suspended ceiling tiles 600 x 1200 Total | 3 | 2
B | 10 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | Bulkhead (tiles)
C | 2 | 2.5 | 0 | 134 | 670 | 0 | 0 | 804 | MODERATE | 3 | 2
A | 3 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | Bulkhead (tiles) Total | 3 | 2
Suspended Ceiling Tile - Metal Total | 15 | 13.4667 | 0 | 134 | 670 | 0 | 0 | 804 | Ceiling Finishes Total | 2.6829 | 2
Exposed underside of stair | [8 empty] | Comfort Cooling
B | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Computer room air conditioning
Exposed underside of stair Total | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Exposed Concrete | [8 empty] | Computer room air conditioning Total | 2 | 2
A | 8 | 57.5 | 0 | 0 | 0 | 0 | 0 | 0 | Comfort Cooling Total | 2 | 2
Exposed Concrete Total | 8 | 57.5 | 0 | 0 | 0 | 0 | 0 | 0 | Cubicles
Mineral fibre suspended ceiling tiles 600 x 1200 | [8 empty] | High Pressure Laminated Chipboard
B | 7 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
C | 3 | 2 | 0 | 5811.72 | 0 | 0 | 0 | 5811.72 | LOW | 2 | 2
Mineral fibre suspended ceiling tiles 600 x 1200 Total | 10 | 7.6 | 0 | 5811.72 | 0 | 0 | 0 | 5811.72 | High Pressure Laminated Chipboard Total | 2.75 | 2
Metal suspended ceiling tiles 600x1200 | [8 empty] | Cubicles Total | 2.75 | 2
B | 3 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | Decorations
Metal suspended ceiling tiles 600x1200 Total | 3 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | Emulsion paint finish to walls
Plasterboard & Skim finish | [8 empty] | MODERATE | 3 | 2
B | 16 | 14.625 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Plasterboard & Skim finish Total | 16 | 14.625 | 0 | 0 | 0 | 0 | 0 | 0 | Emulsion paint finish to walls Total | 2.6111 | 2
Exposed Soffit | [8 empty] | Emulsion paint finish to Ceiling
B | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
A | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | Emulsion paint finish to Ceiling Total | 3 | 2
Exposed Soffit Total | 3 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | Decoration of timber surfaces
Timber boarding | [8 empty] | LOW | 2 | 2
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | Decoration of timber surfaces Total | 2 | 2
Timber boarding Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | Joinery decorations (architraves, skirting)
MDF Boards | [8 empty] | MODERATE | 3 | 2
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
MDF Boards Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | Joinery decorations (architraves, skirting) Total | 2.5 | 2
Bulkhead (tiles) | [8 empty] | Timber surround to rooflight
C | 1 | 2 | 0 | 458.82 | 0 | 0 | 0 | 458.82 | LOW | 2 | 2
Bulkhead (tiles) Total | 1 | 2 | 0 | 458.82 | 0 | 0 | 0 | 458.82 | Timber surround to rooflight Total | 2 | 2
Ceiling Finishes Total | 142 | 12.4789 | 0 | 26360.9159 | 16604.8186 | 0 | 0 | 42965.7345 | Door decorations (internal)
Cold Water Plant & Equipment | [8 empty] | LOW | 2 | 2
Cold Water Storage Tanks | [8 empty] | Door decorations (internal) Total | 2 | 2
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Floor Paint
Cold Water Storage Tanks Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Cold Water Plant & Equipment Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Floor Paint Total | 2 | 2
Comfort Cooling | [8 empty] | Decorations Total | 2.5571 | 2
Refrigerant pipework systems | [8 empty] | Door
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Solid veneer faced timber door (Single) with vision panel
Refrigerant pipework systems Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Condensate pipework system | [8 empty] | Solid veneer faced timber door (Single) with vision panel Total | 3 | 2
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Fire door furniture
Condensate pipework system Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | SIGNIFICANT | 4 | 3
Computer room air conditioning | [8 empty] | Fire door furniture Total | 4 | 3
C | 1 | 1 | 10000 | 0 | 0 | 0 | 0 | 10000 | Door Total | 3.5 | 2.5
Computer room air conditioning Total | 1 | 1 | 10000 | 0 | 0 | 0 | 0 | 10000 | FF&E
Comfort Cooling Total | 5 | 1 | 10000 | 0 | 0 | 0 | 0 | 10000 | Blinds
Communication System | [8 empty] | MODERATE | 3 | 2
Television and satellite systems | [8 empty] | Blinds Total | 3 | 2
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | FF&E Total | 3 | 2
Television and satellite systems Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Floor Finishes
Communication systems | [8 empty] | Carpet Tile
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Communication systems Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Public address systems | [8 empty] | Carpet Tile Total | 2.9062 | 2
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Barrier Matting
Public address systems Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Communication System Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Barrier Matting Total | 3 | 2
Cubicles | [8 empty] | Vinyl tiles
High Pressure Laminated Chipboard | [8 empty] | MODERATE | 3 | 2
C | 4 | 2 | 0 | 5200 | 0 | 0 | 0 | 5200 | LOW | 2 | 2
High Pressure Laminated Chipboard Total | 4 | 2 | 0 | 5200 | 0 | 0 | 0 | 5200 | Vinyl tiles Total | 2.5 | 2
Timber cubicle door | [8 empty] | Raised access tiles
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | SIGNIFICANT | 3 | 4
Timber cubicle door Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | Raised access tiles Total | 3 | 4
Cubicles Total | 5 | 3.2 | 0 | 5200 | 0 | 0 | 0 | 5200 | Sheet Vinyl (slip resistant)
Decorations | [8 empty] | MODERATE | 3 | 2.1667
Emulsion paint finish to walls | [8 empty] | Sheet Vinyl (slip resistant) Total | 3 | 2.1667
B | 63 | 7.746 | 0 | 0 | 0 | 0 | 0 | 0 | Carpet Sheet
C | 54 | 2.7037 | 0 | 1506.0222 | 9448.8264 | 371.7 | 0 | 11326.5486 | MODERATE | 3 | 2
A | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Emulsion paint finish to walls Total | 119 | 5.4286 | 0 | 1506.0222 | 9448.8264 | 371.7 | 0 | 11326.5486 | Carpet Sheet Total | 2.5 | 2
Emulsion paint finish to Ceiling | [8 empty] | Vinyl tile (blistered)
C | 1 | 3 | 0 | 0 | 181.02 | 0 | 0 | 181.02 | MODERATE | 3 | 2
Emulsion paint finish to Ceiling Total | 1 | 3 | 0 | 0 | 181.02 | 0 | 0 | 181.02 | Vinyl tile (blistered) Total | 3 | 2
Decoration of timber surfaces | [8 empty] | Sheet Vinyl
C | 2 | 2.5 | 0 | 14 | 35 | 0 | 0 | 49 | MODERATE | 3 | 2
A | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Decoration of timber surfaces Total | 3 | 3.6667 | 0 | 14 | 35 | 0 | 0 | 49 | Sheet Vinyl Total | 2.5 | 2
Joinery decorations (architraves, skirting) | [8 empty] | Timber boarding (raised floor)
B | 16 | 6.625 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 3
C | 10 | 2.8 | 0 | 49 | 168 | 35 | 0 | 252 | Timber boarding (raised floor) Total | 3 | 3
A | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | Floor Finishes Total | 2.8627 | 2.0784
Joinery decorations (architraves, skirting) Total | 28 | 5.2143 | 0 | 49 | 168 | 35 | 0 | 252 | IPS
Timber surround to rooflight | [8 empty] | High Pressure Laminated Chipboard
C | 1 | 2 | 0 | 10 | 0 | 0 | 0 | 10 | MODERATE | 2.7143 | 2.2857
Timber surround to rooflight Total | 1 | 2 | 0 | 10 | 0 | 0 | 0 | 10 | LOW | 2 | 2
Door decorations (internal) | [8 empty] | High Pressure Laminated Chipboard Total | 2.625 | 2.25
B | 3 | 6.6667 | 0 | 0 | 0 | 0 | 0 | 0 | IPS Total | 2.625 | 2.25
C | 1 | 4 | 0 | 0 | 0 | 39.24 | 0 | 39.24 | Ironmongery
Door decorations (internal) Total | 4 | 6 | 0 | 0 | 0 | 39.24 | 0 | 39.24 | Ironmongery (general item)
Floor Paint | [8 empty] | MODERATE | 3 | 2.75
B | 28 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
C | 1 | 2 | 0 | 150 | 0 | 0 | 0 | 150 | Ironmongery (general item) Total | 2.5714 | 2.4286
Floor Paint Total | 29 | 7.7931 | 0 | 150 | 0 | 0 | 0 | 150 | Door Lever
Decorations Total | 185 | 5.7189 | 0 | 1729.0222 | 9832.8464 | 445.94 | 0 | 12007.8086 | LOW | 2 | 2
Door | [8 empty] | Door Lever Total | 2 | 2
Solid veneer faced timber door (Single) with vision panel | [8 empty] | Lever handle
B | 32 | 10.125 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
C | 1 | 1 | 100 | 0 | 0 | 0 | 0 | 100 | Lever handle Total | 2 | 2
A | 4 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Door closer
Solid veneer faced timber door (Single) with vision panel Total | 37 | 10.9459 | 100 | 0 | 0 | 0 | 0 | 100 | MODERATE | 3 | 2
Solid veneer faced timber door (Single) | [8 empty] | Door closer Total | 3 | 2
B | 50 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | Pull handles
Solid veneer faced timber door (Single) Total | 50 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Solid veneer faced timber door (Double) with vision panel | [8 empty] | Pull handles Total | 2 | 2
B | 6 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | Ironmongery Total | 2.3125 | 2.1875
Solid veneer faced timber door (Double) with vision panel Total | 6 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | Joinery
Hollow core door (Single) | [8 empty] | Timber sub frame / sill / general surfaces
B | 8 | 10.25 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Hollow core door (Single) Total | 8 | 10.25 | 0 | 0 | 0 | 0 | 0 | 0 | Timber sub frame / sill / general surfaces Total | 3 | 2
Fire door furniture | [8 empty] | Ply boxing
D | 1 | 1 | 25 | 0 | 0 | 0 | 0 | 25 | LOW | 2 | 2
Fire door furniture Total | 1 | 1 | 25 | 0 | 0 | 0 | 0 | 25 | Ply boxing Total | 2 | 2
Aluminium fully glazed door | [8 empty] | Joinery Total | 2.5 | 2
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | Mechanical Ventilation
Aluminium fully glazed door Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | Centrifugal fans
Glazed Double Leaf | [8 empty] | LOW | 2 | 2
B | 3 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Centrifugal fans Total | 2 | 2
Glazed Double Leaf Total | 3 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Humidifier
Solid veneer faced timber door (Single+Half) with vision panel | [8 empty] | LOW | 2 | 2
B | 5 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | Humidifier Total | 2 | 2
Solid veneer faced timber door (Single+Half) with vision panel Total | 5 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | Mechanical Ventilation Total | 2 | 2
Steel security door / cell door | [8 empty] | Sink
B | 15 | 15.3333 | 0 | 0 | 0 | 0 | 0 | 0 | Vitreous China
A | 2 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Steel security door / cell door Total | 17 | 15.8824 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Hollow Core door single (with vision panel) | [8 empty] | Vitreous China Total | 2.8 | 2
B | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | Stainless Steel
Hollow Core door single (with vision panel) Total | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 3
Door Total | 130 | 11.1077 | 125 | 0 | 0 | 0 | 0 | 125 | Stainless Steel Total | 3 | 3
FF&E | [8 empty] | Sink Total | 2.8333 | 2.1667
Dumb waiter | [8 empty] | Vanity Unit
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | High Pressure Laminated Chipboard
Dumb waiter Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Laminate worktop on metal legs | [8 empty] | LOW | 2 | 2
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | High Pressure Laminated Chipboard Total | 2.8333 | 2
Laminate worktop on metal legs Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Vanity Unit Total | 2.8333 | 2
Blinds | [8 empty] | Wall Finishes
B | 15 | 7.7333 | 0 | 0 | 0 | 0 | 0 | 0 | Plaster on Brick/Block
C | 4 | 2 | 0 | 600 | 0 | 0 | 0 | 600 | MODERATE | 3 | 2
Blinds Total | 19 | 6.5263 | 0 | 600 | 0 | 0 | 0 | 600 | LOW | 2 | 2
Worktop & units | [8 empty] | Plaster on Brick/Block Total | 2.8 | 2
B | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | Hessian wall panels
A | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Worktop & units Total | 3 | 9.6667 | 0 | 0 | 0 | 0 | 0 | 0 | Hessian wall panels Total | 3 | 2
Metal handrail | [8 empty] | Wall Finishes Total | 2.8125 | 2
B | 2 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | WC
Metal handrail Total | 2 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | Vitreous China
Benches | [8 empty] | MODERATE | 3 | 2
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Vitreous China Total | 3 | 2
Benches Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | WC Total | 3 | 2
Built in cupboards etc | [8 empty] | Grand Total | 2.6783 | 2.0478
B | 2 | 9 | 0 | 0 | 0 | 0 | 0 | 0
Built in cupboards etc Total | 2 | 9 | 0 | 0 | 0 | 0 | 0 | 0
Timber staircase
B | 4 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Timber staircase Total | 4 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Shelfing
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Shelfing Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Laminated reception desk
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Laminated reception desk Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Reception glazing (aluminium framed)
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Reception glazing (aluminium framed) Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Floor mounted fixed timber seating with metal frame
B | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Floor mounted fixed timber seating with metal frame Total | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Grab Rails - Vertical
B | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Grab Rails - Vertical Total | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Grab Rails - Drop down
B | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Grab Rails - Drop down Total | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Hand Rails
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Hand Rails Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Units
B | 3 | 9.3333 | 0 | 0 | 0 | 0 | 0 | 0
A | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Units Total | 4 | 10.75 | 0 | 0 | 0 | 0 | 0 | 0
Benching
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Benching Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Fixed laminate Worktop / desking
B | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Fixed laminate Worktop / desking Total | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen units with laminate worktops
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen units with laminate worktops Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Fixed base timber units
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Fixed base timber units Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Floor mounted seat and counter
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Floor mounted seat and counter Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Fixed wooden bed (vandalised wooden tops)
B | 14 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Fixed wooden bed (vandalised wooden tops) Total | 14 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Dumbwaiter lift
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Dumbwaiter lift Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
FF&E Total | 68 | 9.6029 | 0 | 600 | 0 | 0 | 0 | 600
Floor Finishes
Carpet Tile
B | 25 | 8.32 | 0 | 0 | 0 | 0 | 0 | 0
C | 32 | 2.8438 | 0 | 6422.8204 | 32305.4182 | 0 | 522.96 | 39251.1986
Carpet Tile Total | 57 | 5.2456 | 0 | 6422.8204 | 32305.4182 | 0 | 522.96 | 39251.1986
Barrier Matting
C | 2 | 3 | 0 | 0 | 430.26 | 0 | 0 | 430.26
A | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Barrier Matting Total | 3 | 8.6667 | 0 | 0 | 430.26 | 0 | 0 | 430.26
Vinyl tiles
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
C | 2 | 3 | 0 | 0 | 328.831 | 0 | 0 | 328.831
Vinyl tiles Total | 3 | 4.6667 | 0 | 0 | 328.831 | 0 | 0 | 328.831
Raised access tiles
B | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0
C | 1 | 1 | 30 | 0 | 0 | 0 | 0 | 30
Raised access tiles Total | 3 | 5.6667 | 30 | 0 | 0 | 0 | 0 | 30
Quarry Tiles
B | 9 | 8.8889 | 0 | 0 | 0 | 0 | 0 | 0
Quarry Tiles Total | 9 | 8.8889 | 0 | 0 | 0 | 0 | 0 | 0
Sheet Vinyl (slip resistant)
B | 9 | 8.2222 | 0 | 0 | 0 | 0 | 0 | 0
C | 6 | 1.6667 | 440.684 | 2639.058 | 0 | 0 | 0 | 3079.742
A | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Sheet Vinyl (slip resistant) Total | 16 | 6.1875 | 440.684 | 2639.058 | 0 | 0 | 0 | 3079.742
Carpet Sheet
C | 2 | 3 | 0 | 0 | 878.3016 | 0 | 0 | 878.3016
Carpet Sheet Total | 2 | 3 | 0 | 0 | 878.3016 | 0 | 0 | 878.3016
Vinyl tile (blistered)
C | 1 | 3 | 0 | 0 | 260 | 0 | 0 | 260
Vinyl tile (blistered) Total | 1 | 3 | 0 | 0 | 260 | 0 | 0 | 260
Ceramic tiles
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Ceramic tiles Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Sheet Vinyl
C | 4 | 2.5 | 0 | 336.105 | 1059.8511 | 0 | 0 | 1395.9561
A | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Sheet Vinyl Total | 5 | 4 | 0 | 336.105 | 1059.8511 | 0 | 0 | 1395.9561
Concrete
B | 28 | 45.8929 | 0 | 0 | 0 | 0 | 0 | 0
A | 13 | 51.9231 | 0 | 0 | 0 | 0 | 0 | 0
Concrete Total | 41 | 47.8049 | 0 | 0 | 0 | 0 | 0 | 0
Timber boarding (raised floor)
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
C | 1 | 2 | 0 | 100 | 0 | 0 | 0 | 100
Timber boarding (raised floor) Total | 2 | 7 | 0 | 100 | 0 | 0 | 0 | 100
Floor Finishes Total | 143 | 17.8182 | 470.684 | 9497.9834 | 35262.6619 | 0 | 522.96 | 45754.2893
Fuel Services
Gas distribution pipework
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Gas distribution pipework Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel shut-off valves
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel shut-off valves Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel storage tank.
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel storage tank. Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel Meter & Measurement
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel Meter & Measurement Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel Services Total | 4 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Controls
Control Panels
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Control Panels Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Motorised Control Valves
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Motorised Control Valves Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Controls Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Distribution
Heating Distribution Pipework
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Distribution Pipework Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Services thermal insulation
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Services thermal insulation Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Plant Manual Isolation Valves
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Plant Manual Isolation Valves Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Motorised Actuators
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Motorised Actuators Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Radiators.
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Radiators. Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fan Convectors
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fan Convectors Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Natural Convectors
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Natural Convectors Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
LTHW Warm air heaters
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
LTHW Warm air heaters Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Electric Heaters.
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Electric Heaters. Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Distribution Total | 11 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Plant & Auxiliaries
Gas fired boiler 100kw - 300kw
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Gas fired boiler 100kw - 300kw Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Flue Systems (stainless steel 200 kw boiler)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Flue Systems (stainless steel 200 kw boiler) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Commercial Circulating Pump (Single or dual type)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Commercial Circulating Pump (Single or dual type) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Air-to-air commercial Heat pumps
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Air-to-air commercial Heat pumps Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Plant & Auxiliaries Total | 4 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot & Cold Water Distribution Services
Hot and Cold Water Pipework systems
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot and Cold Water Pipework systems Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot & Cold Water Services thermal insulation
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot & Cold Water Services thermal insulation Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Water Meter & Measurement
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Water Meter & Measurement Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Shower mixer and head
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Shower mixer and head Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot & Cold Water Distribution Services Total | 6 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot Water Plant & Equipment
Circulating Pumps
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Circulating Pumps Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Gas fired hot water heaters
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Gas fired hot water heaters Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Water Boilers - (tea points)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Water Boilers - (tea points) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot Water Plant & Equipment Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Internal glazing
Softwood Timber
B | 7 | 8.5714 | 0 | 0 | 0 | 0 | 0 | 0
A | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Softwood Timber Total | 8 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Metal frame
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
A | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Metal frame Total | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 0
Softwood timber (veneer)
A | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Softwood timber (veneer) Total | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Rooflight with metal frame
B | 14 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Rooflight with metal frame Total | 14 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Softwood Timber (painted)
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Softwood Timber (painted) Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Internal glazing Total | 26 | 10.9231 | 0 | 0 | 0 | 0 | 0 | 0
IPS
High Pressure Laminated Chipboard
B | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0
C | 8 | 2 | 0 | 7150 | 0 | 0 | 0 | 7150
High Pressure Laminated Chipboard Total | 10 | 3.2 | 0 | 7150 | 0 | 0 | 0 | 7150
IPS Total | 10 | 3.2 | 0 | 7150 | 0 | 0 | 0 | 7150
Ironmongery
Ironmongery (general item)
B | 101 | 10.3366 | 0 | 0 | 0 | 0 | 0 | 0
C | 7 | 2.4286 | 0 | 475 | 205 | 0 | 0 | 680
A | 4 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0
Ironmongery (general item) Total | 112 | 10.0982 | 0 | 475 | 205 | 0 | 0 | 680
Door Lever
C | 2 | 2 | 0 | 50 | 0 | 0 | 0 | 50
Door Lever Total | 2 | 2 | 0 | 50 | 0 | 0 | 0 | 50
Lever handle
C | 5 | 2 | 0 | 125 | 0 | 0 | 0 | 125
Lever handle Total | 5 | 2 | 0 | 125 | 0 | 0 | 0 | 125
Door closer
C | 1 | 2 | 0 | 25 | 0 | 0 | 0 | 25
Door closer Total | 1 | 2 | 0 | 25 | 0 | 0 | 0 | 25
Pull handles
C | 1 | 2 | 0 | 25 | 0 | 0 | 0 | 25
Pull handles Total | 1 | 2 | 0 | 25 | 0 | 0 | 0 | 25
Ironmongery Total | 121 | 9.4959 | 0 | 700 | 205 | 0 | 0 | 905
Joinery
Timber skirting
B | 65 | 8.5538 | 0 | 0 | 0 | 0 | 0 | 0
A | 4 | 15.75 | 0 | 0 | 0 | 0 | 0 | 0
Timber skirting Total | 69 | 8.971 | 0 | 0 | 0 | 0 | 0 | 0
Timber dado / picture rail
B | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Timber dado / picture rail Total | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Timber / MDF architraves
B | 93 | 9.8495 | 0 | 0 | 0 | 0 | 0 | 0
A | 4 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0
Timber / MDF architraves Total | 97 | 10.1649 | 0 | 0 | 0 | 0 | 0 | 0
Timber sub frame / sill / general surfaces
B | 24 | 8.1667 | 0 | 0 | 0 | 0 | 0 | 0
C | 1 | 3 | 0 | 0 | 50 | 0 | 0 | 50
Timber sub frame / sill / general surfaces Total | 25 | 7.96 | 0 | 0 | 50 | 0 | 0 | 50
Ply boxing
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
C | 1 | 2 | 0 | 150 | 0 | 0 | 0 | 150
Ply boxing Total | 2 | 6 | 0 | 150 | 0 | 0 | 0 | 150
Timber deck
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Timber deck Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
MDF / Ply panels above window
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
MDF / Ply panels above window Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Panelling to radiator
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Panelling to radiator Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Timber surround to rooflight
B | 3 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Timber surround to rooflight Total | 3 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Metal joinery
B | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Metal joinery Total | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Joinery Total | 222 | 9.2613 | 0 | 150 | 50 | 0 | 0 | 200
Lifting Equipment
Lift Plant & Controls
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lift Plant & Controls Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lifting Equipment Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lighting Systems
Emergency lighting (inc key switch)
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Emergency lighting (inc key switch) Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lighting and luminaires (internal)
B | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lighting and luminaires (internal) Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lighting and luminaires (external)
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lighting and luminaires (external) Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lighting Systems Total | 7 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Mains Power Supplies
LV switchgear (internal)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
LV switchgear (internal) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Main supply switchgear
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Main supply switchgear Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
SWA mains/sub distribution cables.
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
SWA mains/sub distribution cables. Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Earth bonding (Primary)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Earth bonding (Primary) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Electricity Meter & Measurement
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Electricity Meter & Measurement Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Mains Power Supplies Total | 5 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Mechanical Ventilation
Packaged Air handling units
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Packaged Air handling units Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Galvanised Ductwork Systems
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Galvanised Ductwork Systems Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Centrifugal fans
C | 1 | 5 | 0 | 0 | 0 | 0 | 1000 | 1000
Centrifugal fans Total | 1 | 5 | 0 | 0 | 0 | 0 | 1000 | 1000
Ductwork thermal insulation
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Ductwork thermal insulation Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
External louvres steel painted
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
External louvres steel painted Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Humidifier
C | 1 | 1 | 10000 | 0 | 0 | 0 | 0 | 10000
Humidifier Total | 1 | 1 | 10000 | 0 | 0 | 0 | 0 | 10000
Kitchen Extract canopies/ Hoods (average)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Extract canopies/ Hoods (average) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Local extract fans
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Local extract fans Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fire Dampers
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fire Dampers Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Grilles and diffusers
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Grilles and diffusers Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Mechanical Ventilation Total | 13 | 3 | 10000 | 0 | 0 | 0 | 1000 | 11000
Miscellaneous Electrical Equipment & Plant
Kitchen (cooking and support systems)
B | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Kitchen (cooking and support systems) Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous Electrical Equipment & Plant Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous Mechanical Equipment & Plant
Petrol & Diesel Storage and Pumps
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Petrol & Diesel Storage and Pumps Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous Mechanical Equipment & Plant Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Other
Showers
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Showers Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Metal shower
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Metal shower Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Other Total | 2 | 9 | 0 | 0 | 0 | 0 | 0 | 0
Power Generation
Standby generator plus prime mover
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Standby generator plus prime mover Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Power Generation Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Sink
Cleaners sink (Belfast etc)
B | 4 | 11.25 | 0 | 0 | 0 | 0 | 0 | 0
Cleaners sink (Belfast etc) Total | 4 | 11.25 | 0 | 0 | 0 | 0 | 0 | 0
Vitreous China
B | 7 | 8.2857 | 0 | 0 | 0 | 0 | 0 | 0
C | 5 | 2 | 0 | 3761.42 | 0 | 0 | 0 | 3761.42
Vitreous China Total | 12 | 5.6667 | 0 | 3761.42 | 0 | 0 | 0 | 3761.42
Stainless Steel
B | 3 | 9.3333 | 0 | 0 | 0 | 0 | 0 | 0
D | 1 | 1 | 100 | 0 | 0 | 0 | 0 | 100
Stainless Steel Total | 4 | 7.25 | 100 | 0 | 0 | 0 | 0 | 100
Sink Total | 20 | 7.1 | 100 | 3761.42 | 0 | 0 | 0 | 3861.42
Sub-Main Distribution
Sub distribution wiring and containment systems
B | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Sub distribution wiring and containment systems Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fixed appliance power supplies/ isolators (Spurs)
B | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fixed appliance power supplies/ isolators (Spurs) Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Distribution boards (critical)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Distribution boards (critical) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Distribution boards (Non critical)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Distribution boards (Non critical) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Switched socket outlet (SSO)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Switched socket outlet (SSO) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Sub-Main Distribution Total | 9 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Urinal
Vitreous China
B | 4 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0
Vitreous China Total | 4 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0
Urinal Total | 4 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0
Vanity Unit
High Pressure Laminated Chipboard
B | 3 | 7.3333 | 0 | 0 | 0 | 0 | 0 | 0
C | 6 | 2 | 0 | 3900 | 0 | 0 | 0 | 3900
High Pressure Laminated Chipboard Total | 9 | 3.7778 | 0 | 3900 | 0 | 0 | 0 | 3900
Vanity Unit Total | 9 | 3.7778 | 0 | 3900 | 0 | 0 | 0 | 3900
Wall Finishes
Plaster on Brick/Block
B | 107 | 12.1402 | 0 | 0 | 0 | 0 | 0 | 0
C | 15 | 2.2 | 0 | 622.688 | 406.87 | 0 | 0 | 1029.558
A | 4 | 25 | 0 | 0 | 0 | 0 | 0 | 0
Plaster on Brick/Block Total | 126 | 11.3651 | 0 | 622.688 | 406.87 | 0 | 0 | 1029.558
Ceramic Wall Tiles
B | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0
A | 1 | 35 | 0 | 0 | 0 | 0 | 0 | 0
Ceramic Wall Tiles Total | 14 | 14.5714 | 0 | 0 | 0 | 0 | 0 | 0
Metal / timber stud with plasterboard
B | 4 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0
Metal / timber stud with plasterboard Total | 4 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0
Pre-finished panels
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Pre-finished panels Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Exposed Concrete
B | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0
A | 7 | 57.8571 | 0 | 0 | 0 | 0 | 0 | 0
Exposed Concrete Total | 9 | 46.7778 | 0 | 0 | 0 | 0 | 0 | 0
Brickwork
B | 18 | 40 | 0 | 0 | 0 | 0 | 0 | 0
A | 15 | 55 | 0 | 0 | 0 | 0 | 0 | 0
Brickwork Total | 33 | 46.8182 | 0 | 0 | 0 | 0 | 0 | 0
Hessian wall panels
C | 1 | 2 | 0 | 150 | 0 | 0 | 0 | 150
Hessian wall panels Total | 1 | 2 | 0 | 150 | 0 | 0 | 0 | 150
Glazed partitions
B | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0
A | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Glazed partitions Total | 2 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Acoustic Wall Panels
B | 2 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Acoustic Wall Panels Total | 2 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Metal wall panels
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Metal wall panels Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Blockwork
A | 3 | 55 | 0 | 0 | 0 | 0 | 0 | 0
Blockwork Total | 3 | 55 | 0 | 0 | 0 | 0 | 0 | 0
Wall Finishes Total | 196 | 19.9235 | 0 | 772.688 | 406.87 | 0 | 0 | 1179.558
WC
Vitreous China
B | 25 | 8.64 | 0 | 0 | 0 | 0 | 0 | 0
C | 1 | 3 | 0 | 0 | 615.82 | 0 | 0 | 615.82
Vitreous China Total | 26 | 8.4231 | 0 | 0 | 615.82 | 0 | 0 | 615.82
WC Total | 26 | 8.4231 | 0 | 0 | 615.82 | 0 | 0 | 615.82
#N/A
#N/A
(blank) |  |  | 0 | 0 | 0 | 0 | 0 | 0
#N/A Total |  |  | 0 | 0 | 0 | 0 | 0 | 0
#N/A Total |  |  | 0 | 0 | 0 | 0 | 0 | 0
Grand Total | 1390 | 11.7188 | 20695.684 | 59822.0295 | 62978.0169 | 445.94 | 1522.96 | 145464.6304
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.

## Fabric Survey
Condition Ranking | [6 empty] | Priority |  |  | Type
A |  |  | A = Good - Performing as intended and operating efficiently |  |  |  | 1 | Urgent | E | Environmental
B |  |  | B = Satisfactory - performing as intended, exhibiting minor deterioration. |  |  |  | 2 | within 2 years | F | Fire Precaution
C |  |  | C = Poor - exhibiting major defects and/or not operating as intended. |  |  |  | 3 | 3 to 5 years | G | Consequential risk
D |  |  | D = Failed - life expired and/or serious risk imminent failure |  |  |  | 4 | 5 to 10 years | H | Health and Safety
[7 empty] | 5 | 10 to 15 years | I | Further Investigation
[7 empty] | 6 | 15 to 25 years | L | Loss of Service
[9 empty] | Q | Energy
[9 empty] | R | Recommendation
[9 empty] | S | Security
ROOM DESCRIPTION | [6 empty] | CONDITION SURVEY
Internal / External | Building | Room No. / Name | Floor | Element | Element group | Sub element group | Unit rate | Item quantity | Standard Rate | Condition rank | Priority | Type | Typical Life from new (YEARS) | Estimated Remaining Useful Design Life (YEARS) | Cost | Disrepair Narrative / General Comments | Remedial Works | Photo ref: (Applied to "C" or "D" ratings i.e.. C or D) | Current & Impending Backlog Risk Assessment | SCORE RANGE | RISK RANKING | Predicted replacement (£s) | [5 empty] | Total | General Comments
[16 empty] | Disrepair Narrative / General Comments | Remedial Works |  |  | 1 - 5 | Low | 1 | 1-2 | 3-5 | 5-10 | 10-15 | 15-25 |  | Remedial Works
[16 empty] | Disrepair Narrative / General Comments | Remedial Works |  |  | 6 - 10 | Moderate | Priority 1 2019 | Priority 2 2019/2021 | Priority 3 2020/24 | Priority 4 2023/29 | Priority 5 2028/34 | Priority 6 2033/43 |  | Remedial Works
Internal | 1 | Residential rooms | 0 | Internal finishes | Ceiling finishes | Plaster | m2 | 421 | 42 | B | 4 | R | 35 | 5-10 years | 17682 | Plastered ceilings to residential rooms are in good condition | Currently the ceilings are in an acceptable condition, but there may be a necessity to replaster this element in the coming years. | N/A | [6 empty] | 17682 |  |  | 17682
Internal | 1 | Residential rooms | 0 | Internal finishes | Wall finishes | Plaster | m2 | 1248 | 42 | B | 4 | R | 35 | 5-10 years | 52416 | Plastered walls to residential rooms are in good condition | Currently the walls are in an acceptable condition, but there may be a necessity to replaster the surfaces in the coming years. | N/A | [6 empty] | 52416 |  |  | 52416
Internal | 1 | Residential rooms | 0 | Internal finishes | Floor finishes | Vinyl sheet | m2 | 421 | 80 | B | 3 | R | 15 | 3-5 years | 33680 | Residential rooms have vinyl sheet flooring | Currently the vinyl sheet floor covering to the residential rooms are in good condition, however due to the nature of the rooms their condition will deteriorate. | N/A | [5 empty] | 33680 |  |  |  | 33680
Internal | 1 | Residential rooms | 0 | Internal finishes | Floor finishes | Vinyl sheet | m2 | 421 | 80 | A | 5 | R | 15 | 10-15 years | 33680 | Cyclical Replacement | Cyclical Replacement | N/A | [7 empty] | 12896 |  | 12896
Internal | 1 | Residential rooms | 0 | Door | Door | Solid veneer faced FD30 (Single) | nr | 37 | 823 | B | 4 | R | 35 | 5-10 years | 30451 | Timber fire doors to all residential rooms | Upon inspection, every room had a fire door which was in acceptable condition. The doors are likely to be effected by impact damage and so this could be considered when estimating its lifespan. | N/A | [6 empty] | 30451 |  |  | 30451
Internal | 1 | Residential rooms | 0 | Sanitary ware | Sink | Vitreous China | nr | 37 | 525 | B | 6 | R | 35 | 15-25 years | 19425 | Each residential room has a Vitreous China WHB | The vitreous china WHB to each room are in good condition. Due to their low usage they have been given a long estimated lifespan | N/A | [8 empty] | 19425 | 19425
Internal | 1 | Residential rooms | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 1705 | 11 | B | 2 | R | 5 | Within 2 years | 18755 | Each residential room has wallpapered walls, whilst in good condition will require re-papering or redecorating | Due to the nature of the room the walls will need to be included as part of a cyclical maintenance plan. | N/A |  |  |  |  | 18755 |  |  |  |  | 18755
Internal | 1 | Residential rooms | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 1705 | 11 | A | 4 | R | 5 | 5-10 years | 18755 | Cyclical Redecorations | Cyclical Redecorations | N/A | [6 empty] | 18755 |  |  | 18755
Internal | 1 | Residential rooms | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 1705 | 11 | A | 5 | R | 5 | 10-15 years | 18755 | Cyclical Redecorations | Cyclical Redecorations | N/A | [7 empty] | 18755 |  | 18755
Internal | 1 | Residential rooms | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 1705 | 11 | A | 6 | R | 5 | 15-25 years | 18755 | Cyclical Redecorations | Cyclical Redecorations | N/A | [8 empty] | 18755 | 18755
Internal | 1 | Residential rooms | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 1705 | 11 | A | 6 | R | 5 | 15-25 years | 18755 | Cyclical Redecorations | Cyclical Redecorations | N/A | [8 empty] | 18755 | 18755
Internal | 1 | Circulation | 0 | Internal finishes | Ceiling finishes | Plaster | m2 | 345 | 42 | B | 4 | R | 35 | 5-10 years | 14490 | Plastered ceilings to circulation corridors are in good condition | Currently the ceilings are in an acceptable condition, but there may be a necessity to replaster the surfaces in the coming years. | N/A | [6 empty] | 14490 |  |  | 14490
Internal | 1 | Circulation | 0 | Internal finishes | Wall finishes | Plaster | m2 | 345 | 42 | B | 4 | R | 35 | 5-10 years | 14490 | Plastered walls to residential rooms are in good condition | Currently the walls are in an acceptable condition, but there may be a necessity to replaster the surfaces in the coming years. | N/A | [6 empty] | 14490 |  |  | 14490
Internal | 1 | Circulation | 0 | Internal finishes | Floor finishes | Carpet | m2 | 345 | 59 | B | 5 | R | 15 | 10-15 years | 20355 | Circulation corridors have vinyl sheet / carpet flooring | Currently the vinyl sheet / carpet floor covering to the circulation rooms are in good condition, however due to the nature of the rooms their condition will deteriorate. | N/A | [7 empty] | 20355 |  | 20355
Internal | 1 | Circulation | 0 | Door | Door | Solid veneer faced FD30 (Single) | nr | 14 | 823 | B | 4 | R | 35 | 5-10 years | 11522 | Timber fire doors to all residential rooms | Upon inspection, every room had a fire door which was in acceptable condition. The doors are likely to be effected by impact damage and so this could be considered when estimating its lifespan. | N/A | [6 empty] | 11522 |  |  | 11522
Internal | 1 | Circulation | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 840 | 11 | B | 2 | R | 5 | Within 2 years | 9240 | Each circulation room has plastered walls decorated with emulsion | Due to the nature of the room the walls will need to be included as part of a cyclical maintenance plan. | N/A |  |  |  |  | 9240 |  |  |  |  | 9240
Internal | 1 | Circulation | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 840 | 11 | A | 4 | R | 5 | 5-10 years | 9240 | Cyclical Redecorations | Cyclical Redecorations | N/A | [6 empty] | 9240 |  |  | 9240
Internal | 1 | Circulation | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 840 | 11 | A | 5 | R | 5 | 10-15 years | 9240 | Cyclical Redecorations | Cyclical Redecorations | N/A | [7 empty] | 9240 |  | 9240
Internal | 1 | Circulation | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 840 | 11 | A | 6 | R | 5 | 15-25 years | 9240 | Cyclical Redecorations | Cyclical Redecorations | N/A | [8 empty] | 9240 | 9240
Internal | 1 | Circulation | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 840 | 11 | A | 6 | R | 5 | 15-25 years | 9240 | Cyclical Redecorations | Cyclical Redecorations | N/A | [8 empty] | 9240 | 9240
Internal | 1 | Kitchens | 0 | Internal finishes | Ceiling finishes | Plaster | m2 | 47 | 42 | B | 4 | H | 35 | 5-10 years | 1974 | Plastered ceilings to serving / cooking kitchens are in good condition | Currently the ceilings are in an acceptable condition, but there may be a necessity to replaster the surfaces in the coming years. | N/A | [6 empty] | 1974 |  |  | 1974
Internal | 1 | Kitchens | 0 | Internal finishes | Wall finishes | Plaster | m2 | 47 | 42 | B | 4 | H | 35 | 5-10 years | 1974 | Plastered walls to serving / cooking kitchens are in good condition | Currently the walls are in an acceptable condition, but there may be a necessity to replaster the surfaces in the coming years. | N/A | [6 empty] | 1974 |  |  | 1974
Internal | 1 | Kitchens | 0 | Internal finishes | Floor finishes | Vinyl sheet | m2 | 47 | 80 | B | 3 | H | 15 | 3-5 years | 3760 | Serving / cooking kitchens have vinyl sheet flooring | Currently the vinyl sheet floor covering to the serving kitchens / cooking kitchen are in good condition, however due to the nature of the rooms their condition will deteriorate. | N/A | [5 empty] | 3760 |  |  |  | 3760
Internal | 1 | Kitchens | 0 | Door | Door | Solid veneer faced FD30 (Single) | nr | 2 | 823 | B | 4 | H | 35 | 5-10 years | 1646 | Timber fire doors to all serving / cooking kitchens | Upon inspection, every kitchen had a fire door which was in acceptable condition. The doors are likely to be effected by impact damage and so this could be considered when estimating its lifespan. | N/A | [6 empty] | 1646 |  |  | 1646
Internal | 1 | Kitchens | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 115 | 11 | B | 2 | H | 5 | Within 2 years | 1265 | Each serving / cooking kitchen has plastered walls decorated with emulsion | Due to the nature of the room the walls will need to be included as part of a cyclical maintenance plan. | N/A |  |  |  |  | 1265 |  |  |  |  | 1265
Internal | 1 | Kitchens | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 115 | 11 | A | 4 | H | 5 | 5-10 years | 1265 | Cyclical Redecorations | Cyclical Redecorations | N/A | [6 empty] | 1265 |  |  | 1265
Internal | 1 | Kitchens | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 115 | 11 | A | 5 | H | 5 | 10-15 years | 1265 | Cyclical Redecorations | Cyclical Redecorations | N/A | [7 empty] | 1265 |  | 1265
Internal | 1 | Kitchens | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 115 | 11 | A | 6 | H | 5 | 15-25 years | 1265 | Cyclical Redecorations | Cyclical Redecorations | N/A | [8 empty] | 1265 | 1265
Internal | 1 | Kitchens | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 115 | 11 | A | 6 | H | 5 | 15-25 years | 1265 | Cyclical Redecorations | Cyclical Redecorations | N/A | [8 empty] | 1265 | 1265
Internal | 1 | Kitchens | 0 | Sanitary ware | Sink | Stainless steel | nr | 4 | 601 | B | 2 | H | 20 | Within 2 years | 2404 | The kitchen has stainless-steel sinks - which is in acceptable condition | The stainless-steel sinks will need replacing in due course | N/A |  |  |  |  | 2404 |  |  |  |  | 2404
Internal | 1 | Kitchens | 0 | Sanitary ware | Sink | Vitreous China | nr | 4 | 523 | B | 4 | H | 20 | 5-10 years | 2092 | The Kitchen has vitreous china WHB - which is in acceptable condition | The vitreous china sink will need replacing in due course | N/A | [6 empty] | 2092 |  |  | 2092
Internal | 1 | Kitchens | 0 | FF+E | FF+E | Worktops and units | nr | 4 | 500 | B | 4 | H | 10 | 5-10 years | 2000 | The Kitchen has worktop and units (base and wall) | The worktop and units (base and wall) will need replacing in due course | N/A | [6 empty] | 2000 |  |  | 2000
Internal | 1 | Kitchens | 0 | FF+E | FF+E | Worktops and units | nr | 4 | 500 | B | 6 | H | 10 | 15-25 years | 2000 | The Kitchen has worktop and units (base and wall) | The worktop and units (base and wall) will need replacing as part of cyclical maintenance plan | N/A | [8 empty] | 2000 | 2000
Internal | 1 | WC / Bath | 0 | Internal finishes | Ceiling finishes | Plaster | m2 | 85 | 42 | B | 4 | H | 35 | 5-10 years | 3570 | Plastered ceilings to WC / bathrooms corridors are in good condition | Currently the ceilings are in an acceptable condition, but there may be a necessity to replaster the surfaces in the coming years. | N/A | [6 empty] | 3570 |  |  | 3570
Internal | 1 | WC / Bath | 0 | Internal finishes | Wall finishes | Plaster | m2 | 85 | 42 | B | 4 | H | 35 | 5-10 years | 3570 | Plastered walls to WC / bathrooms are in good condition | Currently the walls are in an acceptable condition, but there may be a necessity to replaster the surfaces in the coming years. | N/A | [6 empty] | 3570 |  |  | 3570
Internal | 1 | WC / Bath | 0 | Internal finishes | Floor finishes | Vinyl sheet | m2 | 85 | 80 | B | 3 | H | 15 | 3-5 years | 6800 | WC / bathrooms have vinyl sheet flooring | Currently the vinyl sheet floor covering to the WC / bathrooms are in good condition, however due to the nature of the rooms their condition will deteriorate. | N/A | [5 empty] | 6800 |  |  |  | 6800
Internal | 1 | WC / Bath | 0 | Internal finishes | Floor finishes | Vinyl sheet | m2 | 85 | 80 | B | 5 | H | 10 | 10-15 years | 6800 | WC / bathrooms have vinyl sheet flooring | Currently the vinyl sheet floor covering to the WC / bathrooms are in good condition, however due to the nature of the rooms their condition will deteriorate. | N/A | [7 empty] | 7380 |  | 7380
Internal | 1 | WC / Bath | 0 | Door | Door | Solid veneer faced FD30 (Single) | nr | 17 | 823 | B | 4 | H | 35 | 5-10 years | 13991 | Timber doors to all WC / bathrooms | Upon inspection, every room had a timber door which was in acceptable condition. The doors are likely to be effected by impact damage and so this could be considered when estimating its lifespan. | N/A | [6 empty] | 13991 |  |  | 13991
Internal | 1 | WC / Bath | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 185 | 11 | B | 2 | H | 5 | Within 2 years | 2035 | Each WC / bathroom has plastered walls decorated with emulsion | Due to the nature of the room the walls will need to be included as part of a cyclical maintenance plan. | N/A |  |  |  |  | 2035 |  |  |  |  | 2035
Internal | 1 | WC / Bath | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 185 | 11 | A | 4 | H | 5 | 5-10 years | 2035 | Cyclical Redecorations | Cyclical Redecorations | N/A | [6 empty] | 2035 |  |  | 2035
Internal | 1 | WC / Bath | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 185 | 11 | A | 5 | H | 5 | 10-15 years | 2035 | Cyclical Redecorations | Cyclical Redecorations | N/A | [7 empty] | 2035 |  | 2035
Internal | 1 | WC / Bath | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 185 | 11 | A | 6 | H | 5 | 15-25 years | 2035 | Cyclical Redecorations | Cyclical Redecorations | N/A | [8 empty] | 2035 | 2035
Internal | 1 | WC / Bath | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 185 | 11 | A | 6 | H | 5 | 15-25 years | 2035 | Cyclical Redecorations | Cyclical Redecorations | N/A | [8 empty] | 2035 | 2035
Internal | 1 | WC / Bath | 0 | Sanitary ware | Sink | Vitreous China | nr | 13 | 525 | B | 5 | H | 20 | 10-15 years | 6825 | Each WC / bathrooms has vitreous china WHB | Currently the vitreous china WHB is in good condition, however it need upgrading in due course. | N/A | [7 empty] | 6825 |  | 6825
Internal | 1 | WC / Bath | 0 | Sanitary ware | WC | Vitreous China | nr | 13 | 525 | B | 4 | H | 20 | 5-10 years | 6825 | Each WC / bathrooms has vitreous china WC | Currently the vitreous china WC is in good condition, however it need upgrading in due course. | N/A | [6 empty] | 6825 |  |  | 6825
Internal | 1 | Offices / ancillary rooms | 0 | Internal finishes | Ceiling finishes | Plaster | m2 | 137 | 42 | B | 4 | R | 35 | 5-10 years | 5754 | Plastered ceilings to offices / ancillary rooms are in good condition | Currently the ceilings are in an acceptable condition, but there may be a necessity to replaster the surfaces in the coming years. | N/A | [6 empty] | 5754 |  |  | 5754
Internal | 1 | Offices / ancillary rooms | 0 | Internal finishes | Wall finishes | Plaster | m2 | 137 | 42 | B | 4 | R | 35 | 5-10 years | 5754 | Plastered walls to offices / ancillary rooms are in good condition | Currently the walls are in an acceptable condition, but there may be a necessity to replaster the surfaces in the coming years. | N/A | [6 empty] | 5754 |  |  | 5754
Internal | 1 | Offices / ancillary rooms | 0 | Internal finishes | Floor finishes | Carpet | m2 | 137 | 59 | B | 3 | R | 10 | 3-5 years | 8083 | Offices / ancillary rooms have carpet sheet flooring | Currently the carpet sheet floor covering is in good condition, however due to the nature of the rooms their condition will deteriorate. | N/A | [5 empty] | 8083 |  |  |  | 8083
Internal | 1 | Offices / ancillary rooms | 0 | Internal finishes | Floor finishes | Carpet | m2 | 137 | 59 | B | 6 | R | 10 | 15-25 years | 8083 | Offices / ancillary rooms have carpet sheet flooring | Currently the carpet sheet floor covering is in good condition, however due to the nature of the rooms their condition will deteriorate. Include as part of as cyclical maintenance plan | N/A | [8 empty] | 8083 | 8083
Internal | 1 | Offices / ancillary rooms | 0 | Door | Door | Solid veneer faced FD30 (Single) | nr | 18 | 823 | B | 4 | R | 35 | 5-10 years | 14814 | Timber fire doors to all offices / ancillary rooms | Upon inspection, every room had a fire door which was in acceptable condition. The doors are likely to be effected by impact damage and so this could be considered when estimating its lifespan. | N/A | [6 empty] | 14814 |  |  | 14814
Internal | 1 | Offices / ancillary rooms | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 425 | 11 | B | 2 | R | 5 | Within 2 years | 4675 | Each office / ancillary room, has plastered walls decorated with emulsion | Due to the nature of the room the walls will need to be included as part of a cyclical maintenance plan. | N/A |  |  |  |  | 4675 |  |  |  |  | 4675
Internal | 1 | Offices / ancillary rooms | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 425 | 11 | A | 4 | R | 5 | 5-10 years | 4675 | Cyclical Redecorations | Cyclical Redecorations | N/A | [6 empty] | 4675 |  |  | 4675
Internal | 1 | Offices / ancillary rooms | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 425 | 11 | A | 5 | R | 5 | 10-15 years | 4675 | Cyclical Redecorations | Cyclical Redecorations | N/A | [7 empty] | 4675 |  | 4675
Internal | 1 | Offices / ancillary rooms | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 425 | 11 | A | 6 | R | 5 | 15-25 years | 4675 | Cyclical Redecorations | Cyclical Redecorations | N/A | [8 empty] | 4675 | 4675
Internal | 1 | Offices / ancillary rooms | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 425 | 11 | A | 6 | R | 5 | 15-25 years | 4675 | Cyclical Redecorations | Cyclical Redecorations | N/A | [8 empty] | 4675 | 4675
Internal | 1 | Laundry | 0 | Internal finishes | Ceiling finishes | Plaster | m2 | 22 | 42 | B | 4 | H | 35 | 5-10 years | 924 | Plastered ceilings to Laundry are in good condition | Currently the ceilings are in an acceptable condition, but there may be a necessity to replaster the surfaces in the coming years. | N/A | [6 empty] | 924 |  |  | 924
Internal | 2 | Laundry | 0 | Internal finishes | Ceiling finishes | Plaster | m2 | 67 | 42 | B | 4 | H | 36 | 5-10 years | 2814 | Plastered walls to Laundry are in good condition | Currently the walls are in an acceptable condition, but there may be a necessity to replaster the surfaces in the coming years. | N/A | [6 empty] | 2814 |  |  | 2814
Internal | 1 | Laundry | 0 | Internal finishes | Floor finishes | Vinyl sheet | m2 | 22 | 80 | B | 3 | H | 10 | 3-5 years | 1760 | Vinyl sheet flooring to Laundry is in good condition | Currently the vinyl sheet flooring to the Laundry is in good condition, however due to the nature of the room its condition will deteriorate. | N/A | [5 empty] | 1760 |  |  |  | 1760
Internal | 1 | Laundry | 0 | Internal finishes | Floor finishes | Vinyl sheet | m2 | 22 | 80 | B | 5 | H | 10 | 10-15 years | 1760 | Vinyl sheet flooring to Laundry is in good condition | Currently the vinyl sheet flooring to the Laundry is in good condition, however due to the nature of the room its condition will deteriorate. | N/A | [7 empty] | 1760 |  | 1760
Internal | 1 | Laundry | 0 | Door | Door | Solid veneer faced FD30 (Single) | nr | 1 | 823 | B | 4 | H | 35 | 5-10 years | 823 | Timber door to Laundry is in a good condition | Upon inspection, every room had a fire door which was in acceptable condition. The doors are likely to be effected by impact damage and so this could be considered when estimating its lifespan. | N/A | [6 empty] | 823 |  |  | 823
Internal | 1 | Laundry | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 231 | 11 | B | 2 | H | 5 | Within 2 years | 2541 | Each office / ancillary room, has plastered walls decorated with emulsion | Due to the nature of the room the walls will need to be included as part of a cyclical maintenance plan. | N/A |  |  |  |  | 2541 |  |  |  |  | 2541
Internal | 1 | Laundry | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 89 | 11 | A | 4 | H | 5 | 5-10 years | 979 | Cyclical Redecorations | Cyclical Redecorations | N/A | [6 empty] | 979 |  |  | 979
Internal | 1 | Laundry | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 89 | 11 | A | 5 | H | 5 | 10-15 years | 979 | Cyclical Redecorations | Cyclical Redecorations | N/A | [7 empty] | 979 |  | 979
Internal | 1 | Laundry | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 89 | 11 | A | 6 | H | 5 | 15-25 years | 979 | Cyclical Redecorations | Cyclical Redecorations | N/A | [8 empty] | 979 | 979
Internal | 1 | Laundry | 0 | Internal finishes | Decorations | Complete decoration of room including ceilings, walls, joinery and internal face of doors | m2 | 89 | 11 | A | 6 | H | 5 | 15-25 years | 979 | Cyclical Redecorations | Cyclical Redecorations | N/A | [8 empty] | 979 | 979
External | 1 | External | 0 | Building superstructure | Roofs - pitched | Concrete tiles | m2 | 1068 | 93 | B | 5 | R | 40 | 10-15 years | 99324 | Concrete roof tiles to pitched roof - good condition | Whilst the tiles have technically reached the end of their expected life - it is estimated they will remain functional for a further 10 - 15 years | N/A | [7 empty] | 99324 |  | 99324
External | 1 | External | 0 | Building superstructure | Roofs - pitched | Concrete tiles | m | 60 | 24 | C | 2 | R | 40 | Within 2 years | 1440 | Cracked and spalled mortar joints to verge tiles require re-pointing | Repoint mortar to verges | N/A |  |  |  |  | 1440 |  |  |  |  | 1440
External | 1 | External | 0 | Building superstructure | Roofs - flat | Mineral-felt roof covering | m2 | 240 | 160 | B | 2 | R | 15 | Within 2 years | 38400 | Whilst performing reasonably well, the roofs are clearly reaching the end of their shelf life and have experienced failure in recent years. | Recover flat roofs including uplift for cut-to falls insulation | N/A |  |  |  |  | 38400 |  |  |  |  | 38400
External | 1 | External | 0 | Building superstructure | Soffits / Fascia's | Timber ship-lap boarding | m | 210 | 55 | C | 3 | R | 10 | 3-5 years | 11550 | Timber fascia-boards | Due to the exposed location of the shiplap boarding - it is likely that they will need replacement in 3-5 years | N/A | [5 empty] | 11550 |  |  |  | 11550
External | 1 | External | 0 | Building superstructure | Roof - drainage | PVCu gutters & downpipes | m | 95 | 96 | B | 5 | R | 25 | 10-15 years | 9120 | PVC RWG are in acceptable condition with no signs of defect | Cyclical Replacement | N/A | [7 empty] | 9120 |  | 9120
External | 1 | External | 0 | Building superstructure | Wall structure | Brickwork | m2 | 0 | 0 | B | 6 | R | 85 | 15-25 years | 0 | Exposed brickwork in good condition without defects | No works required | N/A | [9 empty] | 0
External | 1 | External | 0 | Building superstructure | Windows (inc grilles/louvres) | S/G timber windows | m2 | 101 | 757 | B | 3 | R | 25 | 3-5 years | 76457 | S/G timber framed windows | Replace with D/G aluminium units for improved thermal and acoustic efficiency | N/A | [5 empty] | 76457 |  |  |  | 76457
External | 1 | External | 0 | Building superstructure | Doors | Powder coated aluminium | nr | 0 | 0 | B | 6 | R | 25 | 15-25 years | 0 | Aluminium double-glazed door units | No works required | N/A | [9 empty] | 0
External areas | 1 | External | 0 | Fencing | Fencing & Security | Anti-climb fencing | m | 320 | 148 | B | 5 | R | 15 | 10-15 years | 47360 | 2m high weldmesh, anticlimb fencing to perimeter of site | The weldmesh, anticlimb fencing is in good condition but will ned a further upgrade within the lifespan of this survey | [8 empty] | 47360 |  | 47360
External areas | 1 | External | 0 | External Landscaping | Hard Landscaping | Tarmacadam | m2 | 120 | 66 | B | 4 | R | 20 | 5-10 years | 7920 | Tarmacadam's access road | The access road was in acceptable condition with no potholes etc to note. Cyclical scarify and new wear coat | [7 empty] | 7920 |  |  | 7920
External areas | 1 | External | 0 | Ramps & Steps | Ramp | Ramps to exit doors | nr | 14 | 2500 | B | 5 | R | 30 | 10-15 years | 35000 | Concrete ramps leading to external exits | Good condition | [8 empty] | 35000 |  | 35000
Internal | 1 | Ground Floor Switchroom | 0 | Electrical Services | Sub-mains switchgear | Distribution Boards | Item | 1 | 5000 | C | 1 | R | 25 | Urgent | 5000 | Existing main distribution is obsolete and rewirable fuse board | Replace the existing main distribution board with a new MCCB panel board. | N/A |  |  |  | 5000 | [5 empty] | 5000
Internal | 1 | Sluice rooms | 0 | Electrical Services | Sub-mains switchgear | Distribution Boards | Item | 6 | 1500 | C | 1 | H | 25 | Urgent | 9000 | Replace all of the existing rewirable fuse boards. | Replace the board with a new distribution boards | N/A |  |  |  | 9000 | [5 empty] | 9000
Internal | 1 | Circulation areas | 0 | Electrical Services | Mains Power Supplies | SWA mains/sub distribution cables. | Item | 1 | 3000 | C | 1 | R | 25 | Urgent | 3000 | Replace the existing sub-mains cable supplies to all distribution boards in the building | The existing mains cabling is nearing the end of its useful life and may be short when being reconnected into the new panel board. Cables are already being extended with different colour cables at remote end and the cable should be reinstalled and sized to suit the latest version of BS7671. | N/A |  |  |  | 3000 | [5 empty] | 3000
Internal | 1 | Bedrooms | 0 | Electrical Services | Lighting Systems | Emergency lighting (Inc. key switch) | Item | 40 | 200 | C | 1 | R | 5 | Urgent | 8000 | Bedrooms should be provided with an emergency luminaire | Install a recessed anti-panic emergency luminaire with a new kept test switch. | N/A |  |  |  | 8000 | [5 empty] | 8000
Internal | 1 | Bedrooms | 0 | Electrical Services | Lighting Systems | Lighting and luminaires (internal) | Item | 40 | 40 | C | 1 | R | 20 | Urgent | 1600 | The existing bedroom pendant luminaire should be provided with a dimmable LED lamp and | Install new LED luminaires to allow for the residents to be able to read and for nursing staff/doctors to be able to carry out medical examinations in the bed rooms. | N/A |  |  |  | 3000 | [5 empty] | 3000
Internal | 1 | Bedrooms | 0 | Electrical Services | Lighting Systems | Lighting and luminaires (internal) | Item | 40 | 200 | C | 1 | R | 20 | Urgent | 8000 | The general lighting to be supplemented with additional LED recessed down lighters to provide good light levels | Install additional LED down lighters to bedrooms | N/A |  |  |  | 8000 | [5 empty] | 8000
Internal | 1 | Bedrooms | 0 | Electrical Services | Lighting Systems | Lighting control and management systems | Item | 1 | 3000 | C | 2 | R | 20 | within 2 years | 3000 | Light switches should be replaced with new switches with colour contrast colour plates and new dimmer switches for the pendant luminaire should be installed. | Replace the existing light switches with new switches. | N/A |  |  |  |  | 3000 |  |  |  |  | 3000
Internal | 1 | Bedrooms | 0 | Electrical Services | Protection Systems | Fire Alarm Installations (Inc., call points, sounders and detection) | Item | 1 | 7500 | C | 1 | R | 25 | Urgent | 7500 | The bedroom should be provided with a sounder and a beacon/VAD. | Upgrade the fire alarm system two include all necessary smoke detector, VAD's and sounders. | N/A |  |  |  | 7500 | [5 empty] | 7500
Internal | 1 | Building | 0 | Electrical Services | Protection Systems | Fire Alarm Installations (Inc., call points, sounders and detection) | Item | 1 | 5000 | C | 1 | R | 25 | Urgent | 5000 | Not all of the rooms within the building have been provided with automatic detection. | The fire alarm system should be upgraded to bring the system to L1 + M level of detection. | N/A |  |  |  | 5000 | [5 empty] | 5000
Internal | 1 | Corridors | 0 | Electrical Services | Lighting Systems | Emergency lighting (Inc. key switch) | Item | 1 | 10000 | C | 1 | R | 25 | Urgent | 10000 | The corridors should be provided with illuminated emergency exit signs and installed at all turns and exits from internal rooms. | A review of the current exit signage should be carried out and where the signs do not comply with BS5266, new signs should be installed. | N/A |  |  |  | 10000 | [5 empty] | 10000
Internal | 1 | Corridors | 0 | Electrical Services | Lighting Systems | Lighting and luminaires (internal) | Item | 1 | 12000 | C | 2 | R | 25 | within 2 years | 12000 | The existing corridor and amenity area luminaires should be replaced with new LED luminaires to improve energy efficiency. | Install new LED luminaires. | N/A |  |  |  |  | 12000 |  |  |  |  | 12000
Internal | 1 | Corridors | 0 | Electrical Services | Lighting Systems | Lighting control and management systems | Item | 1 | 5000 | C | 2 | R | 25 | within 2 years | 5000 | The corridor lighting should be provided with a photocell lighting controls to make use of natural daylight. | All corridor lighting controls should be reviewed and where possible automatic lighting controls should be installed in the corridors. | N/A |  |  |  |  | 5000 |  |  |  |  | 5000
Internal | 1 | Building | 0 | Electrical Services | Sub-mains switchgear | Switched socket outlet (SSO) | Item | 1 | 5000 | C | 2 | R | 25 | within 2 years | 5000 | Existing small power outlet plates should be of a contrast colour to the walls. | All corridor small power accessories should be replaced with new accessories with a contrasting colour finish to the wall. | N/A |  |  |  |  | 5000 |  |  |  |  | 5000
Internal | 1 | Building | 0 | Electrical Services | Sub-mains switchgear | Sub distribution wiring and containment systems | Item | 1 | 10000 | C | 2 | R | 25 | within 2 years | 10000 | Rewire the building to bring the system up to current standards. | Rewire the building including all small power and lighting accessories. | N/A |  |  |  |  | 10000 |  |  |  |  | 10000
Internal | 1 | Boiler houses | 0 | Mechanical Services | Heating Plant & Auxiliaries | Heating Pressurisation Unit | Item | 3 | 1000 | C | 2 | R | 20 | within 2 years | 3000 | The Mikrofill pressurisation unit is outdated and should be replaced with latest model as per the other boiler houses. | Install Mikrofill pressurisation unit. | N/A |  |  |  |  | 3000 |  |  |  |  | 3000
Internal | 1 | Boiler house | 0 | Mechanical Services | Heating Plant & Auxiliaries | Dosing Pots | Item | 4 | 300 | D | 1 | R | 15 | Urgent | 1200 | No dosing pots installed on heating systems. | Dosing pots to be installed on each heating system | N/A |  |  |  | 1200 | [5 empty] | 1200
Internal | 1 | Boiler house | 0 | Mechanical Services | Heating Plant & Auxiliaries | Magnetic Filters | Item | 4 | 500 | D | 1 | R | 10 | Urgent | 2000 | If New boilers are installed on existing old heating systems, install magnetic filters to protect boilers/pumps | Magnetic filters to be installed on each heating system | N/A |  |  |  | 2000 | [5 empty] | 2000
Internal | 1 | Boiler house | 0 | Mechanical Services | Heating Plant & Auxiliaries | Pressure relief discharges/Tundish | Item | 15 | 125 | D | 1 | H | 20 | Urgent | 1875 | Many of the various pressure relief discharges do not discharge into tundishes but directly onto the floor. This is a health and safety hazard. | All discharges to terminate within a tundish and connected directly to a drain. | N/A |  |  |  | 1875 | [5 empty] | 1875
Internal | 1 | Boiler house | 0 | Mechanical Services | Heating Plant & Auxiliaries | Expansion Vessels | Item | 4 | 250 | D | 1 | R | 15 | Urgent | 1000 | Expansion vessels do not appear to have correct number of valves and drain off points. To be reviewed. | Expansion vessels need to be reviewed and valves drain off points installed if required. | N/A |  |  |  | 1000 | [5 empty] | 1000
Internal | 1 | Boiler house | 0 | Mechanical Services | Heating Distribution | Heating Services Thermal Insulation | Item | 4 | 350 | D | 1 | Q | 30 | Urgent | 1400 | Heating pipework within boiler houses have insulation to the majority of pipework, but there are a number of sections of missing insulation. All valves to be provided with insulated jackets | Install thermal insulation to all missing sections of pipework within boiler houses and install insulation jackets to all valves. | N/A |  |  |  | 1400 | [5 empty] | 1400
Internal | 1 | Throughout | 0 | Mechanical Services | Heating Distribution | Heating Distribution Pipework | Item | 1 | 20000 | B | 2 | R | 25 | within 2 years | 20000 | Existing distribution is coming to end of life and is a one pipe heating circuit throughout. | Replace existing one pipe heating distribution system with a new 2 pipe heating distribution system. | N/A |  |  |  |  | 20000 |  |  |  |  | 20000
Internal | 1 | Throughout | 0 | Mechanical Services | Heating Distribution | Radiators | Item | 100 | 400 | B | 2 | R | 20 | within 2 years | 40000 | Existing panel and LST radiators are now at end of life and looking very tired and outdated. | Replace all existing radiators with new LST radiators and thermostatic mixing valves. | N/A |  |  |  |  | 40000 |  |  |  |  | 40000
Internal | 1 | Boiler house | 0 | Mechanical Services | Heating Controls | BMS | Item | 1 | 10000 | C | 2 | R | 20 | within 2 years | 10000 | Existing controls are old and very basic | The existing basic controls should be considered to be replaced with a more energy efficient BMS system to control all heating and hot water systems. | N/A |  |  |  |  | 10000 |  |  |  |  | 10000
Internal | 1 | Throughout | 0 | Mechanical Services | Hot & Cold Water Distribution Services | Hot and Cold Water Pipework | Item | 1 | 25000 | C | 2 | R | 25 | within 2 years | 25000 | Existing distribution is coming to end of life. | Replace existing hot and cold water distribution system with a new. | N/A |  |  |  |  | 25000 |  |  |  |  | 25000
Internal | 1 | W.C.'s | 0 | Electrical Services | Communication Services | Toilets | Item | 20 | 300 | C | 2 | H | 25 | within 2 years | 6000 | Wi-Fi access to the internet for all bedrooms | Install 2 No IT/Data cables from the data rack to each of the bedroom corridors and install a Wi-Fi module in each corridor. | N/A |  |  |  |  | 6000 |  |  |  |  | 6000
External | 1 | External | 0 | Electrical Services | Lighting Systems | Lighting and luminaires (external) | Item | 1 | 11500 | C | 2 | R | 25 | within 2 years | 11500 | The existing external walkways do not have any external lighting currently installed to allow persons to move around the side after dark, some of these need to be emergency luminaires. | Install new LED luminaires to the external walkways around the building. | N/A |  |  |  |  | 11500 |  |  |  |  | 11500
Internal | 1 | Boiler house | 0 | Mechanical Services | Fuel Services | Gas distribution pipework | Item | 4 | 750 | D | 2 | R | 20 | within 2 years | 3000 | There are no gas solenoid valves fitted to the gas mains where they enter the boiler houses. | Install a new gas solenoid valve and provide a plantroom stop button linked to the boiler control panel and interlock with the fire alarm system. | N/A |  |  |  |  | 3000 |  |  |  |  | 3000
[17 empty] | Priority Totals |  |  |  |  | 0 | 80755 | 142090 | 254445 | 276969 | 103406
[26 empty] | Overall Total |  | 1077140
857665
1077140

## Lookup - Fabric Int
CODE | Element Ref: | ELEMENT | EG Ref: | ELEMENT GROUP | SE Ref: | SUB ELEMENT GROUP | INDICATIVE LIFE / YEARS | STANDARD RATE | RATE TYPE/ Item, M2, Nr | Cost Notes
10101 | 1 | Internal Finishes | 101 | Ceiling Finishes | 10101 | Suspended Ceiling Tile - Metal | 25 | 134 | m2
10102 | 1 | Internal Finishes | 101 | Ceiling Finishes | 10102 | Mineral fibre suspended ceiling tiles 600 x 600 | 25 | 76.47 | m2 | 1 Man houre and materials from BCIS | Labour set at £23.82/hrs
10103 | 1 | Internal Finishes | 101 | Ceiling Finishes | 10103 | Plasterboard & Skim finish | 35 | 31.9 | m2 | 1 Man houre and materials from BCIS
10104
10105 | 1 | Internal Finishes | 101 | Ceiling Finishes | 10105 | Mineral fibre suspended ceiling tiles 600 x 1200 | 25 | 152.94 | m2 | 1 Man houre and materials from BCIS
10106 | 1 | Internal Finishes | 101 | Ceiling Finishes | 10106 | Exposed Concrete | 85 | 80 | m2
10107 | 1 | Internal Finishes | 101 | Ceiling Finishes | 10107 | Plaster | 35 | x | m2
10108DS | 1 | Internal Finishes | 101 | Ceiling Finishes | 10108DS | Exposed underside of stair | 35 | x | m2
10109 |  | Internal Finishes | 101 | Ceiling Finishes | 10109 | Other 1
10201 | 1 | Internal Finishes | 102 | Wall Finishes | 10201 | Metal / timber stud with plasterboard | 35 | 80 | m2
10202 | 1 | Internal Finishes | 102 | Wall Finishes | 10202 | Blockwork | 85 | 280 | m2
10203 | 1 | Internal Finishes | 102 | Wall Finishes | 10203 | Brickwork | 85 | 265 | m2
10204 | 1 | Internal Finishes | 102 | Wall Finishes | 10204 | Glazed partitions | 30 | TBC | m2
10205 | 1 | Internal Finishes | 102 | Wall Finishes | 10205 | Ceramic Wall Tiles | 35 | 110 | m2 | Hack off and replace with new tiles 200 x 200 including pointing and labour.
10206 | 1 | Internal Finishes | 102 | Wall Finishes | 10206 | Exposed Concrete | 85 | 80 | m2
10207 | 1 | Internal Finishes | 102 | Wall Finishes | 10207 | Plaster on Brick/Block | 35 | 35.38 | m2
10208DS | 1 | Internal Finishes | 102 | Wall Finishes | 10208DS | Pre-finished panels | 25 | x | m2
10301 | 1 | Internal Finishes | 103 | Floor Finishes | 10301 | Sheet Vinyl | 10 | 32.01 | m2 | Labour and mat's from BCIS
10302 | 1 | Internal Finishes | 103 | Floor Finishes | 10302 | Carpet Tile | 15 | 43.58 | m2 | Labour and mat's from BCIS
10303 | 1 | Internal Finishes | 103 | Floor Finishes | 10303 | Carpet Sheet | 15 | 35.02 | m2 | Labour and mat's from BCIS
10304 | 1 | Internal Finishes | 103 | Floor Finishes | 10304 | Concrete | 85 | 80 | m2 | Labour and mat's from BCIS
10305 | 1 | Internal Finishes | 103 | Floor Finishes | 10305 | Quarry Tiles | 15 | 34.3 | m2 | Labour and mat's from BCIS
10306 | 1 | Internal Finishes | 103 | Floor Finishes | 10306 | Sheet Vinyl (slip resistant) | 15 | 42.05 | m2 | Labour and mat's from BCIS
10307 | 1 | Internal Finishes | 103 | Floor Finishes | 10307 | Metal Check Deck | 20 | 24 | m2
10308DS |  | Internal Finishes | 103 | Floor Finishes | 10308DS | Barrier Matting | 20 | 71.71 | m2
10309DS | 1 | Internal Finishes | 103 | Floor Finishes | 10309DS | Vinyl tiles | 15 | 42.05 | m2
10310DS | 1 | Internal Finishes | 103 | Floor Finishes | 10310DS | Raised access tiles | 20 | x | m2
10311 | 1 | Internal Finishes | 103 | Floor Finishes | 10311 | Other | x | x | x
10401 | 1 | Internal Finishes | 104 | Decorations | 10401 | Emulsion paint finish to walls | 5 | 5.31 | m2 | Prepare, 1st coat to previously painted walls. BCIS
10402 | 1 | Internal Finishes | 104 | Decorations | 10402 | Heavy Duty Emulsion Paint Finish | 5 | 7.12 | m2 | Prepare, 1st coat + additional coat to previously painted walls. BCIS
10403 | 1 | Internal Finishes | 104 | Decorations | 10403 | Eggshell paint finish to walls | 5 | 7.12 | m2 | Prepare, 1st coat + additional coat to previously painted walls. BCIS
10404 | 1 | Internal Finishes | 104 | Decorations | 10404 | Decoration to Steel Beams | 7 | 5.13 | m2
10405 | 1 | Internal Finishes | 104 | Decorations | 10405 | Floor Paint | 15 | 25 | m2 | Labour and mat's from BCIS
10406 | 1 | Internal Finishes | 104 | Decorations | 10406 | Emulsion paint finish to Ceiling | 5 | 8.62 | m2 | Labour and mat's from BCIS
10407 | 1 | Internal Finishes | 104 | Decorations | 10407 | Door decorations (internal) | 5 | 6.54 | m2
10408 | 1 | Internal Finishes | 104 | Decorations | 10408 | Decoration of inside window frame | 5 | 5.31 | m2
10409 | 1 | Internal Finishes | 104 | Decorations | 10409 | Joinery decorations (architraves, skirting) | 5 | 7 | m2
10410DS | 1 | Internal Finishes | 104 | Decorations | 10410DS | Decoration of timber surfaces | 5 | 7 | m2
10411 | 1 | Internal Finishes | 104 | Decorations | 10411 | Other 1 | x | x | x
10412 | 1 | Internal Finishes | 104 | Decorations | 10412 | Other 2 | x | x | x
20101 | 2 | Door | 201 | Door | 20101 | Hollow core door (Single) | 20 | 120.73 | Nr
20102 | 2 | Door | 201 | Door | 20102 | Solid veneer faced timber door (Single) | 25 | 157.52 | Nr | Spons page 440
20103 | 2 | Door | 201 | Door | 20103 | Solid veneer faced timber door (Single) with vision panel | 25 | 334 | Nr | Spons page 439
20104 | 2 | Door | 201 | Door | 20104 | Solid veneer faced timber door (Single+Half) | 25 | 445.64 | Nr | Spons page 439
20105 | 2 | Door | 201 | Door | 20105 | Solid veneer faced timber door (Single+Half) with vision panel | 25 | 465.64 | Nr | Spons page 439
20106 | 2 | Door | 201 | Door | 20106 | Solid veneer faced timber door (Double) | 25 | 241.46 | Nr | Spons page 439
20107 | 2 | Door | 201 | Door | 20107 | Solid veneer faced timber door (Double) with vision panel | 25 | 668 | Nr | Spons page 439
20108 | 2 | Door | 201 | Door | 20108 | Glazed Single Leaf | 30 | 140 | Nr
20109 | 2 | Door | 201 | Door | 20109 | Glazed Double Leaf | 30 | 280 | Nr
20110 | 2 | Door | 201 | Door | 20110 | Metal Roller Shutter | 20 | 1309 | Nr | Spons page 444 (3000mm x 1000mmm)
20111 | 2 | Door | 201 | Door | 20111 | Aluminium door with factory applied powder coat finish | 35 | 486 | Nr
20112 | 2 | Door | 201 | Door | 20112 | Steel security door / cell door | 40 | x | x
20113DS | 2 | Door | 201 | Door | 20113DS | Fire door furniture | 25 | x | Item
20114 | 2 | Door | 201 | Door | 20114 | Other 1 | x | x | x
30101 | 3 | Ironmongery | 301 | Ironmongery | 30101 | Ironmongery (general item) | 20 | x | Item
40101 | 4 | Joinery | 401 | Joinery | 40101 | Timber / MDF architraves | 25 | 8.6 | lm
40102 | 4 | Joinery |  | Joinery | 40102 | Timber skirting | 25 | 7 | lm
40103DS | 4 | Joinery |  | Joinery | 40103DS | Timber dado / picture rail | 25 | 7 | lm
40104DS | 4 | Joinery |  | Joinery | 40104DS | Timber sub frame / sill / general surfaces | 25 | 7 | lm
40105DS | 4 | Joinery |  | Joinery | 40105DS | Ply boxing | 25 | 38.4 | m
40105 | 4 | Joinery |  | Joinery | 40105 | Other | x | x | x
50101 | 5 | Sanitary ware | 501 | WC | 50101 | Vitreous China | 20 | 307.91 | Item | Remove and replace with new + labour BCIS
50102 | 5 | Sanitary ware | 501 | WC | 50102 | Stainless Steel | 20 | 473.5 | Item
50201 | 5 | Sanitary ware | 502 | Sink | 50201 | Vitreous China | 20 | 289.34 | Item | Remove and replace with new + labour BCIS
50202 | 5 | Sanitary ware | 502 | Sink | 50202 | Stainless Steel | 20 | 473.5 | Item | Remove and replace with new + labour BCIS
50203 | 5 | Sanitary ware | 502 | Sink | 50203 | Cleaners sink (Belfast etc) | 20 | 307.91 | Nr | Remove and replace with new + labour BCIS
50301 | 5 | Sanitary ware | 503 | Urinal | 50301 | Vitreous China | 15 | 609.85 | Item | Remove and replace with new + labour BCIS
50302 | 5 | Sanitary ware | 503 | Urinal | 50302 | Stainless Steel | 20 | 609.85 | Item | Remove and replace with new + labour BCIS
50401 | 5 | Sanitary ware | 504 | Vanity Unit | 50401 | High Pressure Laminated Chipboard | 20 | 650 | Item |  | http://www.washroomcubicles.co.uk/healthcare-ips-panel-system/
50501 | 5 | Sanitary ware | 505 | Cubicles | 50501 | High Pressure Laminated Chipboard | 20 | 650 | Item
50601 | 5 | Sanitary ware | 506 | IPS | 50601 | High Pressure Laminated Chipboard | 20 | 650 | Item
50701 | 5 | Sanitary ware | 507 | Other | 50701 | Other | x | x | x
60101 | 6 | Windows | 601 | Internal glazing | 60101 | Metal frame | 35 | TBC | Nr
60102 | 6 | Windows | 601 | Internal glazing | 60102 | Softwood Timber | 25 | 50.28 | Nr | Remove and replace with new + labour BCIS
60103 | 6 | Windows | 601 | Internal glazing | 60103 | PVCu Double Glazed Unit | 35 | 350 | Nr
60104 | 6 | Windows | 601 | Internal glazing | 60104 | Other | x | x | x
70101 | 7 | FF&E | 701 | FF&E | 70101 | Grab Rails - Vertical | 20 | 27.41 | Nr | cost per item and labour at £23.82/hrs | Commercial washrooms
70102 | 7 | FF&E | 701 | FF&E | 70102 | Grab Rails - Drop down | 20 | 42.91 | Nr | cost per item and labour at £23.82/hrs | Commercial washrooms
70103 | 7 | FF&E | 701 | FF&E | 70103 | Hand Rails | 20 | 27.41 | Nr | cost per item and labour at £23.82/hrs | Commercial washrooms
70104 | 7 | FF&E | 701 | FF&E | 70104 | Soap dispensers | 10 | 1 | Item
70105 | 7 | FF&E | 701 | FF&E | 70105 | Kitchen Units | 15 | 1 | Item
70106 | 7 | FF&E | 701 | FF&E | 70106 | Paper towel dispensers | x | TBC | Nr
70107 | 7 | FF&E | 701 | FF&E | 70107 | Toilet paper dispensers | x | TBC | Nr
70108 | 7 | FF&E | 701 | FF&E | 70108 | Metal Access Stairs | 25 | Varies | Item
70109DS | 7 | FF&E | 701 | FF&E | 70109DS | Laminate worktop on metal legs | 15 |  | Item
70110DS | 7 | FF&E | 701 | FF&E | 70110DS | Blinds | 15 | x | Item
70111DS | 7 | FF&E | 701 | FF&E | 70111DS | Worktop & units | 15 | x | Item
70112DS | 7 | FF&E | 701 | FF&E | 70112DS | Benches | 20 | x | Item
70113DS | 7 | FF&E | 701 | FF&E | 70113DS | Built in cupboards etc | 20 | x | Item
70114DS | 7 | FF&E | 701 | FF&E | 70114DS | Roller racking | 20 |  | Item
70115DS | 7 | FF&E | 701 | FF&E | 70115DS | Metal handrail | 20 |  | Item
70116DS | 7 | FF&E | 701 | FF&E | 70116DS | Timber staircase | 35 |  | Item
70117 | 7 | FF&E | 701 | FF&E | 70117 | Other | x | x | x

## Lookup - Fabric Ext
CODE | Element Ref: | ELEMENT | EG Ref: | ELEMENT GROUP | SE Ref: | SUB ELEMENT GROUP | INDICATIVE LIFE / YEARS | STANDARD RATE | RATE TYPE/ Item, M2, Nr | Cost Notes
10101 | 1 | External Landscaping | 101 | Hard Landscaping | 10101 | Tarmacadam | 20 |  | m2
10102 |  |  |  |  | 10102 | Concrete | 30 |  | m2
10103 |  |  |  |  | 10103 | Block Paving | 30 |  | m2
10104 |  |  |  |  | 10104 | Paving Slabs | 30 |  | m2
10201 |  |  | 102 | Soft Landscaping | 10201 | Shrubs & Bushes | 20 |  | Item
10202 |  |  |  |  | 10202 | Grass | 20 |  | m2
20101 | 2 | Roads and Car Parks | 201 | Roads | 20101 | Tarmacadam | 20 |  | m2
20201 |  |  | 202 | Car Parks | 20201 | Tarmacadam | 20 |  | m2
30101 | 3 | Street Furniture | 301 | Bollards | 30101 | Concrete | 30 |  | Item
30102 |  |  |  |  | 30102 | Brushed Aluminium | 25 |  | Item
30103 |  |  |  |  | 30103 | Mild Steel | 20 |  | Item
30201 |  |  | 302 | Benches | 30201 | Timber | 20 |  | Item
30202 |  |  |  |  | 30202 | GRP | 35 |  | Item
30203 |  |  |  |  | 30203 | Metal | 25 |  | Item
40101 | 4 | Building Superstructure | 401 | Roofs - Pitched | 40101 | Slate tile | 75 |  | m2
40102 |  |  |  |  | 40102 | Concrete Tiles | 40 |  | m2
40103 |  |  |  |  | 40103 | Clay tiles | 65 |  | m2
40104 |  |  |  |  | 40104 | Other |  |  | m2
40201 |  |  | 402 | Roofs - Flat | 40201 | Single Ply Membrane | 25 |  | m2
40202 |  |  |  |  | 40202 | Built up Felt System | 20 |  | m2
40203 |  |  |  |  | 40203 | Other
40301 |  |  | 403 | Roof Drainage | 40301 | Pressed Metal Gutters & Downpipes | 20 |  | lm
40302 |  |  |  |  | 40302 | Cast Iron Gutters & Downpipes | 50 |  | lm
40303 |  |  |  |  | 40303 | PVCu Gutters & Downpipes | 25 |  | lm
40304 |  |  |  |  | 40304 | Aluminium Gutters & Downpipes | 30 |  | lm
40305 |  |  |  |  | 40305 | Clearing of gutters | 5 |  | lm
40401 |  |  | 404 | Roof Lights | 40401 | Aluminium Framed Glazing | 30 |  | Nr
40402 |  |  |  |  | 40402 | Proprietary Unit | 25 |  | Nr
40403 |  |  |  |  | 40403 | Velux Window | 25 |  | Nr
40501 |  |  | 405 | Wall Structure | 40501 | Blockwork | 85 |  | m2
40502 |  |  |  |  | 40502 | Brickwork | 85 |  | m2
40503 |  |  |  |  | 40503 | Steel | 85 |  | m2
40504 |  |  |  |  | 40504 | Concrete | 80 |  | m2
40505 |  |  |  |  | 40505 | Modular | 30 |  | m2
40506 |  |  |  |  | 40506 | Other
40601 |  |  | 406 | Wall Finishes | 40601 | Ceramic Tiles | 25 |  | m2
40602 |  |  |  |  | 40602 | Plaster | 50 |  | m2
40603 |  |  |  |  | 40603 | Timber | 25 |  | m2
40604 |  |  |  |  | 40604 | Render Plaster | 25 |  | m2
40605 |  |  |  |  | 40605 | Proprietary Cladding | 40 |  | m2
40606 |  |  |  |  | 40606 | Glazing Curtain Wall | 60 |  | m2
40607 |  |  |  |  | 40607 | Brickwork | 40 |  | m2
40608 |  |  |  |  | 40608 | Blockwork | 30 |  | m2
40609 |  |  |  |  | 40609 | Aluminium Cladding | 40 |  | m2
40701 |  |  | 407 | Decorations | 40701 | External block / brick | 5
40702 |  |  |  |  | 40702 | Timber doors | 5
40703 |  |  |  |  | 40703 | Timber windows | 5
40704 |  |  |  |  | 40704 | Metal doors | 5
40705 |  |  |  |  | 40705 | Metal windows | 5
40706 |  |  |  |  | 40706 | Emulsion to render | 5
40707 |  |  |  |  | 40707 | cast iron RWGs | 5
40708 |  |  |  |  | 40708 | Timber generally (soffits/fascias) | 5
40709 |  |  |  |  | 40709 | Other | 5
40801 |  |  | 408 | Soffits / fascias | 40801 | Timber | 15 |  | m2
40802 |  |  |  |  | 40802 | PVCu | 25 |  | m2
40803 |  |  |  |  | 40803 | Aluminium | 30
40901 |  |  | 409 | Upper Floors | 40901 | Cast In-situ Concrete | 80 |  | m2
40902 |  |  |  |  | 40902 | Block & Beam | 80 |  | m2
40903 |  |  |  |  | 40903 | Steel | 85 |  | m2
40904 |  |  |  |  | 40904 | Suspended timber | 70
41001 |  |  | 410 | Windows (inc grilles/louvres) | 41001 | Powder Coated Aluminium | 45 |  | Nr
41002 |  |  |  |  | 41002 | Metal | 45 |  | Nr
41003 |  |  |  |  | 41003 | Softwood Timber | 35 |  | Nr
41004 |  |  |  |  | 41004 | PVCu Double Glazed Unit | 35 |  | Nr
41005 |  |  |  |  | 41005 | Alum. Louvres | 45
41006 |  |  |  |  | 41006 | Alum. Grilles | 45
41101 |  |  | 411 | Doors | 41101 | Powder Coated Aluminium | 30 |  | Nr
41102 |  |  |  |  | 41102 | PVCu Double Glazed Unit | 30 |  | Nr
41103 |  |  |  |  | 41103 | Glazed Doors | 30 |  | Nr
41104 |  |  |  |  | 41104 | Metal Lourve Door | 30 |  | Nr
41105 |  |  |  |  | 41105 | High Speed Fabric Door | 25 |  | Nr
41201 |  |  | 412 | Frame | 41201 | Concrete | 80 |  | m2
41202 |  |  |  |  | 41202 | Steel | 85 |  | m2
41203 |  |  |  |  | 41203 | L/B brickwork | 85
41301 |  |  | 413 | Roof frame | 41301 | Timber | 70
41302 |  |  |  |  | 41302 | Steel | 85
41401 |  |  | 414 | Stairs | 41401 | Concrete | 85 |  | Nr
41402 |  |  |  |  | 41402 | Steel | 85 |  | Nr
41501 |  |  | 415 | External canopies / structures | 41501 | Canopies fixed to block
41502 |  |  |  |  | 41502 | Freestading canopy
41503 |  |  |  |  | 41503 | Bike Shelter
41504 |  |  |  |  | 41504 | Smoking Shelter
41601 |  |  | 416 | Balustrades & Handrails | 41601 | Timber | 25 |  | lm
41602 |  |  |  |  | 41602 | Metal | 35 |  | lm
50101 | 5 | Fencing | 501 | Fencing & Security | 50101 | Concrete post & wire | 25 |  | m2
50102 |  |  |  |  | 50102 | Timber post & wire | 20 |  | m2
50103 |  |  |  |  | 50103 | Timber boards | 15 |  | m2
50104 |  |  |  |  | 50104 | Concrete posts | 25 |  | lm
50105 |  |  |  |  | 50105 | Chain link | 20 |  | lm
50106 |  |  |  |  | 50106 | Mild steel railings | 12 |  | lm
50107 |  |  |  |  | 50107 | Wrought iron railings | 25 |  | lm
50108 |  |  |  |  | 50108 | Galvanised/painted | 20 |  | lm
50109 |  |  |  |  | 50109 | Galanised security gates | 20 |  | Nr
50110 |  |  |  |  | 50110 | Other | x
60101 | 6 | Sub Structure | 601 | Foundations | 60101 | Concrete | 110 |  | lm
7

## Element look up - M+E
Element Ref: | ELEMENT | EG Ref: | ELEMENT GROUP | SE Ref: | SUB ELEMENT GROUP | INDICATIVE LIFE / YEARS | REDUCED LIFE DUE TO USAGE | STANDARD RATE | RATE TYPE/ Item, M2, Nr
1 | Mechanical Services | 101 | Heating Plant & Auxiliaries | 10101 | Gas fired boiler <100kw | 20 | 12 |  | Nr
|  |  |  | 10102 | Gas fired boiler 100kw - 300kw | 25 | 15 |  | Nr
|  |  |  | 10103 | Gas fired boiler 300kw - 500kw | 25 | 20 |  | Nr
|  |  |  | 10104 | Gas fired boiler 500kw + | 25 | 20 |  | Nr
|  |  |  | 10105 | Flue Systems (stainless steel 200 kw boiler) | 30 | 25 |  | Nr
|  |  |  | 10106 | Fan Flues Systems. | 25 | 15 |  | Item
|  |  |  | 10107 | Commerical Circulating Pump (Single or dual type) | 20 | 15 |  | Nr
|  |  |  | 10108 | Centrifugal pumps | 20 | 15 |  | Nr
|  |  |  | 10109 | Heating pressurisation unit | 20 | 20 |  | Nr
|  |  |  | 10110 | Combined heating / chilled water pressurisation unit | 20 | 20 |  | Nr
|  |  |  | 10111 | Expansion vessel (unvented hot water) | 15 | 10 |  | Nr
|  |  |  | 10112 | Gas fired warm air heaters. | 20 | 20 |  | Nr
|  |  |  | 10113 | Dosing pots | 15 | 15 |  | Nr
|  |  |  | 10114 | Sump and well pumps | 12 | 12 |  | Nr
|  |  |  | 10115 | Air-to-air commercial Heat pumps | 15 | 15 |  | Nr
|  |  |  | 10116 | Water-to-air commerical Heat pumps | 15 | 15 |  | Nr
|  |  |  | 10117 | Water treatment equipment | 15 | 15 |  | Item
|  | 102 | Heating Distribution | 10201 | Heating Distribution Pipework | 25 | 25 |  | m2
|  |  |  | 10202 | Heating Services thermal insulation | 30 | 30 |  | m2
|  |  |  | 10203 | Plant Manual Isolation Valves | 25 | 15 |  | Item
|  |  |  | 10204 | Radiators. | 20 | 20 |  | Nr
|  |  |  | 10205 | Radiant Panels | 20 | 20 |  | Nr
|  |  |  | 10206 | Fan Convectors | 20 | 15 |  | Nr
|  |  |  | 10207 | Natural Convectors | 20 | 20 |  | Nr
|  |  |  | 10208 | Underfloor heating steel pipes & Manifolds | 30 | 15 |  | m2
|  |  |  | 10209 | LTHW Warm air heaters | 15 | 15 |  | Nr
|  |  |  | 10210 | Electric Heaters. | 10 | 10 |  | Nr
|  |  |  | 10211 | Expansion Bellow. | 10 | 10 |  | Nr
[5 empty] | Motorised Actuators | 10
|  |  |  | 10212 | Steam Pipework system | 25 | 20 |  | m2
|  | 103 | Heating Controls | 10301 | Building Management Systems | 15 | 15 |  | Item
|  |  |  | 10302 | Control Panels | 20 | 15 |  | Nr
|  |  |  | 10303 | Motorised Control Valves | 15 | 15 |  | Nr
|  | 104 | Fuel Services | 10401 | Gas distribution pipework | 25 | 25 |  | m2
|  |  |  | 10402 | Oil distribution pipework | 25 | 25 |  | m2
|  |  |  | 10403 | Fuel Booster Pumps | 15 | 15 |  | Nr
|  |  |  | 10404 | Fuel shut-off valves | 25 | 20 |  | Nr
|  |  |  | 10405 | Fuel storage tank. | 20 | 20 |  | Nr
|  |  |  | 10406 | Medical Gases | 20 | 20 |  | m2
|  |  |  | 10407 | Fuel Meter & Measurement | 20 | 20 |  | Item
|  | 105 | Cold Water Plant & Equipment | 10501 | Mains cold water booster | 15 | 15 |  | Nr
|  |  |  | 10502 | Cold Water Storage Tanks | 25 | 20 |  | Nr
|  |  |  | 10503 | Sprinkler | 20 | 20 |  | m2
|  | 106 | Hot & Cold Water Distribution Services | 10601 | Hot and Cold Water Pipework systems | 25 | 25 |  | m2
|  |  |  | 10602 | Hot & Cold Water Services thermal insulation | 30 | 20 |  | m2
|  |  |  | 10603 | Hot water temperature mixing valve | 10 |  |  | Nr
|  |  |  | 10604 | Shower mixer and head | 10 | 10 |  | Nr
|  |  |  | 10605 | Water Meter & Measurement | 20 | 15 |  | Item
|  | 107 | Hot Water Plant & Equipment | 10701 | Calorifiers (Copper/ Mild Steel) | 20 | 15 |  | Nr
|  |  |  | 10702 | Circulating Pumps | 15 | 15 |  | Nr
|  |  |  | 10703 | Electric hot water heaters | 15 | 10 |  | Nr
|  |  |  | 10704 | Gas fired hot water heaters | 20 | 15 |  | Nr
|  |  |  | 10705 | Heat Exchanger (Plate / Shell and tube) | 20 | 10 |  | Nr
|  |  |  | 10706 | Water Boilers - (tea points) | 15 | 10 |  | Nr
|  | 108 | Mechanical Ventilation | 10801 | Packaged Air handling units | 20 | 20 |  | Nr
|  |  |  | 10802 | Roof mounted units fans | 15 | 15 |  | Nr
|  |  |  | 10803 | Axial fans (inline) | 15 | 15 |  | Nr
|  |  |  | 10804 | Centrifugal fans | 20 | 15 |  | Nr
|  |  |  | 10805 | Local extract fans | 10 | 10 |  | Nr
|  |  |  | 10806 | Stair / lobby ventilation | 20 | 20 |  | Item
|  |  |  | 10807 | Galvanised Ductwork Systems | 40 | 40 |  | m2
|  |  |  | 10808 | Ductwork thermal insulation | 30 | 30 |  | m2
|  |  |  | 10809 | External louvres steel painted | 20 | 20 |  | Nr
|  |  |  | 10810 | Fire Dampers | 10 | 10 |  | Nr
|  |  |  | 10811 | Grilles and diffusers | 25 | 25 |  | Nr
|  |  |  | 10812 | Humidifier | 15 | 15 |  | Nr
|  |  |  | 10813 | VAV terminal units | 15 | 15 |  | Nr
|  |  |  | 10814 | Kitchen Extract canopies/ Hoods (average) | 30 | 20 |  | Item
|  |  |  | 10815 | Ductwork Heating/ cooiling coils | 25 | 20 |  | Item
|  | 109 | Chilled Water Plant & Equipment | 10901 | Absorption / Centrifugal Chiller 100kw - 300kw | 25 | 20 |  | Nr
|  |  |  | 10902 | Absorption / Centrifugal Chiller 300kw - 500kw | 25 | 20 |  | Nr
|  |  |  | 10903 | Absorption / Centrifugal Chiller 500kw + | 25 | 20 |  | Nr
|  |  |  | 10904 | Circulating Commerical Pump (single or dual type) | 20 | 15 |  | Nr
|  |  |  | 10905 | Refrigerant leak detector | 10 | 10 |  | Item
|  |  |  | 10906 | Trace heating | 20 | 15 |  | m2
|  |  |  | 10907 | Air cooled/ Evaporative condensers | 20 | 15 |  | Nr
|  |  |  | 10908 | Chilled Water storage vessel | 20 | 20 |  | Nr
|  |  |  | 10909 | Chilled Water pressurisation unit | 20 | 20 |  | Nr
|  |  |  | 10910 | Chilled Water Pipework & Valve | 25 | 25 |  | m2
|  |  |  | 10911 | Chilled Water Services thermal insulation | 30 | 20 |  | m2
|  | 110 | Comfort Cooling | 11001 | Fan coil units (heating and cooling) | 15 | 15 |  | Nr
|  |  |  | 11002 | Split systems | 10 | 10 |  | Nr
|  |  |  | 11003 | Computer room air conditioning | 15 | 15 |  | Item
|  |  |  | 11004 | Air conditioning terminal units chilled beams | 20 | 20 |  | Nr
|  |  |  | 11005 | Refrigerant pipework systems | 30 | 30 |  | m2
|  |  |  | 11006 | Condensate pipework system | 15 | 15 |  | m2
|  |  |  | 11007 | VRV units | 15 | 15 |  | Nr
|  | 111 | Miscellaneous Mechanical Equipment & Plant | 11101 | Air compressor | 20 | 20 |  | Nr
|  |  |  | 11102 | Compressed air reciever | 20 | 20 |  | Nr
|  |  |  | 11103 | Pneumatic controls lampsom | 20 | 15 |  | Item
|  |  |  | 11104 | Other |  |  |  | Nr
2 | Electrical Services | 201 | Mains Power Supplies | 20101 | HV switchgear (external) | 30 | 30 |  | Item
|  |  |  | 20102 | Transformers (dry type) | 30 | 30 |  | Nr
|  |  |  | 20103 | LV switchgear (internal) | 25 | 25 |  | Item
|  |  |  | 20104 | Main supply switchgear | 30 | 30 |  | Item
|  |  |  | 20105 | SWA mains/sub distribution cables. | 35 | 35 |  | m2
|  |  |  | 20106 | Earth bonding (Primary) | 30 | 30 |  | Item
|  |  |  | 20107 | Electricity Meter & Measurement | 20 | 20 |  | Item
|  | 202 | Sub-Main Distribution | 20201 | Consumer units | 20 | 20 |  | Nr
|  |  |  | 20202 | Distribution boards (critical) | 20 | 20 |  | Nr
|  |  |  | 20203 | Distribution boards (Non critical) | 20 | 20 |  | Nr
|  |  |  | 20204 | Feeder pillar | 20 | 20 |  | Nr
|  |  |  | 20205 | Inverters | 10 | 10 |  | Nr
|  |  |  | 20206 | Sub distribution wiring and containment systems | 25 | 25 |  | m2
|  |  |  | 20207 | Fixed appliance power supplies/ isolators (Spurs) | 25 | 25 |  | Nr
|  |  |  | 20208 | Switched socket outlet (SSO) | 20 | 20 |  | Nr
|  | 203 | Lighting Systems | 20301 | Emergency lighting (inc key switch) | 25 | 20 |  | Nr
|  |  |  | 20302 | Lighting and luminaires (external) | 15 | 15 |  | Nr
|  |  |  | 20303 | Lighting and luminaires (internal) | 20 | 20 |  | Nr
|  |  |  | 20304 | Lighting control and management systems | 15 | 15 |  | Item
|  | 204 | Protection Systems | 20401 | Access control | 15 | 15 |  | Item
|  |  |  | 20402 | Closed Circuit Television (CCTV) | 20 | 15 |  | m2
|  |  |  | 20403 | Nurse Call Alarm | 15 | 15 |  | m2
|  |  |  | 20404 | Distress Call Alarm | 15 | 15 |  | Item
|  |  |  | 20405 | Fire Alarm Installations (inc, call points, sounders and detection) | 20 | 20 |  | m2
|  |  |  | 20406 | Computer room fire extinguishing system | 15 | 15 |  | m2
|  |  |  | 20407 | Wet/ Dry Riser | 25 | 25 |  | Item
|  |  |  | 20408 | Smoke ventilation systems | 30 | 30 |  | Item
|  |  |  | 20409 | Intruder alarms and intercommunications | 15 | 15 |  | m2
|  |  |  | 20410 | Lightning protection | 25 | 25 |  | m2
|  |  |  | 20411 | Leak Detection | 10 | 10 |  | m2
|  | 205 | Communication System | 20501 | Communication systems | 20 | 20 |  | m2
|  |  |  | 20502 | Public address systems | 20 | 15 |  | m2
|  |  |  | 20503 | Television and satelite systems | 15 | 15 |  | m2
|  | 206 | Lifting Equipment | 20601 | Lift Plant & Controls | 30 | 25 |  | Item
|  |  |  | 20602 | Lift Car refurbishment | 15 | 15 |  | Item
|  |  |  | 20603 | Stair Lifts | 20 | 15 |  | Item
|  |  |  | 20604 | Lifting Hoists | 20 | 15 |  | Item
|  | 207 | Power Generation | 20701 | Combined heat and power (CHP) (gas fired) | 20 | 15 |  | Nr
|  |  |  | 20702 | Standby genernator plus prime mover | 30 | 30 |  | Item
|  |  |  | 20703 | Uninterruptible power supply (UPS) systems | 20 | 20 |  | Item
|  | 208 | Miscellaneous Electrical Equipment & Plant | 20801 | Hand dryer | 5 | 5 |  | Nr
|  |  |  | 20802 | Incinerators | 15 | 15 |  | Item
|  |  |  | 20803 | Kitchen (cooking and support systems) | 15 | 15 |  | Item
|  |  |  | 20804 | Laundries (equipment and support systems) | 20 | 20 |  | Item
|  |  |  | 20805 | Photocoltaic panels | 25 | 25 |  | Nr
|  |  |  | 20806 | Open door with obstacle detector | 20 | 20 |  | Item
|  |  |  | 20807 | Mechanical Roller Shutter Doors | 15 | 15 |  | Item
|  |  |  | 20808 | Theatre clocks | 15 | 15 |  | Item
|  |  |  | 20809 | Other |  |  |  | Nr

## Master Sheet Summary
Item | Description of Work | Quantity | Unit | Cost | Total Cost
New Bassett House HOP - 25 Yr Master Cost Plan
1 | Preliminaries | 1 | Item | 0 | 0
2 | Ceilings | 1 | Item | 47208 | 47208
3 | External walls, windows & Doors | 1 | Item | 76457 | 76457
4 | Floors and Stairs | 1 | Item | 104557 | 104557
5 | Internal Walls & Doors | 1 | Item | 151451 | 151451
6 | Redecorations | 1 | Item | 186307 | 186307
7 | Roofs | 1 | Item | 159834 | 159834
8 | Sanitary Services | 1 | Item | 37571 | 37571
9 | Fixed Furniture and Fittings | 1 | Item | 4000 | 4000
9 | External Areas | 1 | Item | 90280 | 90280
10 | Mechanical Services | 1 | Item | 108475 | 108475
11 | Electrical Services | 1 | Item | 111000 | 111000
12 | Sub-total |  |  |  | 1077140
.
13 | Preliminaries People and Equipment (Based on 15%) |  |  |  | 161571
.
14 | Preliminaries Site Specific Costs (scaffold etc,,,) |  |  |  | 30000
15 | Provisional Uplift for Sectional Works @ 25% |  |  |  | 317177.75
16 | Sub-total |  |  |  | 1585888.75
17 | Pre Construction costs:EMPA @ 3.25% |  |  |  | 0
18 | Sub-total |  |  |  | 1585888.75
19 | Contractor Management Fee @ 3.25% |  |  |  | 0
20 | Sub-total |  |  |  | 1585888.75
21 | Statutory and consultancy fees (includes Building Control, Building Surveyor, Building Services, surveys etc.) @ 15% |  |  |  | 237883.3125
22 | Sub-total |  |  |  | 1823772.0625
23 | Risk Allowance @ 10% |  |  |  | 182377.2063
24 | Client Contingency @10% |  |  |  | 182377.2063
25 | Sub-total |  |  |  | 2188526.475
26 | Professional fees, surveys and stat fees (15%) |  |  |  | 328278.9713
27 | Total Construction Cost |  |  |  | 2516805.4463
Note: All costs to be read in conjunctions with the list of assumptions and clarifications as defined within the report, as well as the information detailed within the report wording.
Note: Provisional uplift of 25% for sectional works included. Actual uplift would need to be established on a site by site basis based on the site layout, extent of works required and the practicalities of undertaking that works with minimal disrupion.

## Roofing
DERBYSHIRE COUNTY COUNCIL
Estimate Cost Plan -Ladycross House
2018-01-01
Item | Description of Work | Quantity | Unit | Cost | Total Cost
Ladycross House
Roofing Project Works
1 | Preliminaries | 1 | Item |  | 0
1.01 | The contractor is to provide safe and sufficient scaffolding access with safety guardrails to enable full access to all areas of work. | 1 | Item | 0 | 0
1.02 | The contractor is to provide suitable and sufficient protection of property and people for the duration of the works. | 1300 | m2 | 5 | 6500
1.03 | The contractor is to allow for cleaning ensuring all debris is removed from site, including making good of damaged surfaces. | 1 | Psum | 1500 | 1500
1.04 | The contractor to allow for the provision of skips for the removal of all waste materials. | 10 | Item | 300 | 3000
1.05 | The contractor to allow for the removal and reinstatement of all external fixtures and fittings. | 1 | Psum | 2500 | 2500
3 | Roofs | 1 | Item | #REF! | #REF!
3.01 | Recovering the existing felt flat roof, including all insulation, flashings and rainwater goods. |  | Note
3.02 | See full condition survey data and summary report for further cost break down. |  | Note
11 | Sub-total |  |  |  | #REF!
.
12 | Preliminaries People and Equipment (Based on 15%) |  |  |  | #REF!
.
13 | Preliminaries Site Specific Costs |  |  |  | 0
14 | Sub-total |  |  |  | #REF!
15 | Pre Construction costs:EMPA @ 3.25% |  |  |  | #REF!
16 | Sub-total |  |  |  | #REF!
17 | Contractor Management Fee @ 3.25% |  |  |  | #REF!
18 | Sub-total |  |  |  | #REF!
19 | Statutory and consultancy fees (includes Building Control, Building Surveyor, Building Services, surveys etc.) @ 15% |  |  |  | #REF!
20 | Sub-total |  |  |  | #REF!
21 | Risk Allowance @ 10% |  |  |  | #REF!
22 | Client Contingency @10% |  |  |  | #REF!
23 | Sub-total |  |  |  | #REF!
24 | Scape Fee @ 0.95% |  |  |  | #REF!
25 | Total Construction Cost |  |  |  | #REF!
Note: All costs to be read in conjunctions with the list of assumptions and clarifications as defined within the report, as well as the information detailed within the report wording.

## Room refurbishment
DERBYSHIRE COUNTY COUNCIL
Estimate Cost Plan -Ladycross House
2018-01-01
Item | Description of Work | Quantity | Unit | Cost | Total Cost
Ladycross House
Room Refurbishment Project Works
1 | Preliminaries | 1 | Item |  | 0
1.01 | The contractor is to provide safe and sufficient scaffolding access with safety guardrails to enable full access to all areas of work. | 1 | Item | 5302.5 | 5302.5
1.02 | The contractor is to provide suitable and sufficient protection of property and people for the duration of the works. | 1400 | m2 | 5 | 7000
1.03 | The contractor is to allow for cleaning ensuring all debris is removed from site, including making good of damaged surfaces. | 1 | Psum | 500 | 500
1.04 | The contractor to allow for the provision of skips for the removal of all waste materials. | 10 | Item | 300 | 3000
1.05 | The contractor to allow for the removal and reinstatement of all external fixtures and fittings. | 1 | Psum | 1000 | 1000
2 | Internal Walls, Ceilings and Doors | 1 | Item | #REF! | #REF!
2.01 | Include for all internal finishes that are life expired, unon-compliant or do not meet the suitability requirements |  | Note
2.02 | See full condition survey data and summary report for further cost break down. |  | Note
3 | Floors and Stairs | 1 | Item | #REF! | #REF!
3.01 | Sumarise required works |  | Note
3.02 | See full condition survey data and summary report for further cost break down. |  | Note
4 | Fixed furniture and fittings | 1 | Item | #REF! | #REF!
4.01 | Sumarise required works |  | Note
4.02 | See full condition survey data and summary report for further cost break down. |  | Note
5 | Decorations | 1 | Item | #REF! | #REF!
5.01 | Sumarise required works |  | Note
5.02 | See full condition survey data and summary report for further cost break down. |  | Note
6 | Sub-total |  |  |  | #REF!
.
7 | Preliminaries People and Equipment (Based on 15%) |  |  |  | #REF!
.
8 | Preliminaries Site Specific Costs |  |  |  | 0
9 | Sub-total |  |  |  | #REF!
10 | Pre Construction costs:EMPA @ 3.25% |  |  |  | #REF!
11 | Sub-total |  |  |  | #REF!
12 | Contractor Management Fee @ 3.25% |  |  |  | #REF!
13 | Sub-total |  |  |  | #REF!
14 | Statutory and consultancy fees (includes Building Control, Building Surveyor, Building Services, surveys etc.) @ 15% |  |  |  | #REF!
15 | Sub-total |  |  |  | #REF!
16 | Risk Allowance @ 10% |  |  |  | #REF!
17 | Client Contingency @10% |  |  |  | #REF!
18 | Sub-total |  |  |  | #REF!
19 | Scape Fee @ 0.95% |  |  |  | #REF!
20 | Total Construction Cost |  |  |  | #REF!
Note: All costs to be read in conjunctions with the list of assumptions and clarifications as defined within the report, as well as the information detailed within the report wording.

## M&E critical works
DERBYSHIRE COUNTY COUNCIL
Estimate Cost Plan -Ladycross House
2018-01-01
Item | Description of Work | Quantity | Unit | Cost | Total Cost
Ladycross House
Mechanical and Electrial works package
1 | Preliminaries | 1 | Item |  | 16802.5
1.01 | The contractor is to provide safe and sufficient scaffolding access with safety guardrails to enable full access to all areas of work. | 1 | Item | 5302.5 | 5302.5
1.02 | The contractor is to provide suitable and sufficient protection of property and people for the duration of the works. | 1400 | m2 | 5 | 7000
1.03 | The contractor is to allow for cleaning ensuring all debris is removed from site, including making good of damaged surfaces. | 1 | Psum | 500 | 500
1.04 | The contractor to allow for the provision of skips for the removal of all waste materials. | 10 | Item | 300 | 3000
1.05 | The contractor to allow for the removal and reinstatement of all external fixtures and fittings. | 1 | Psum | 1000 | 1000
2 | Mechanical Services | 1 | Item | #REF! | #REF!
2.01 | Replacement of fan coiled units to A Block, undertake detailed review of heating controls to A Block and cleaning of mechanical extract in toilet areas in A Block and B Block. |  | Note
2.02 | See full condition survey data and summary report for further cost break down. |  | Note
3 | Electrical Services | 1 | Item | #REF! | #REF!
3.01 | Replace existing light fitting with new LED and replace life expired fire alarm systems to A and B Block. |  | Note
3.02 | See full condition survey data and summary report for further cost break down. |  | Note
4 | Builders work in connection | 1 | Item | #REF! | #REF!
4.01 | Take down ceilings, reinsate compartmentation etc… |  | Note
4.02 | See full condition survey data and summary report for further cost break down. |  | Note
5 | Sub-total |  |  |  | #REF!
.
6 | Preliminaries People and Equipment (Based on 15%) |  |  |  | #REF!
.
7 | Preliminaries Site Specific Costs |  |  |  | 16802.5
8 | Sub-total |  |  |  | #REF!
9 | Pre Construction costs:EMPA @ 3.25% |  |  |  | #REF!
10 | Sub-total |  |  |  | #REF!
11 | Contractor Management Fee @ 3.25% |  |  |  | #REF!
12 | Sub-total |  |  |  | #REF!
13 | Statutory and consultancy fees (includes Building Control, Building Surveyor, Building Services, surveys etc.) @ 15% |  |  |  | #REF!
14 | Sub-total |  |  |  | #REF!
15 | Risk Allowance @ 10% |  |  |  | #REF!
16 | Client Contingency @10% |  |  |  | #REF!
17 | Sub-total |  |  |  | #REF!
18 | Scape Fee @ 0.95% |  |  |  | #REF!
19 | Total Construction Cost |  |  |  | #REF!
Note: All costs to be read in conjunctions with the list of assumptions and clarifications as defined within the report, as well as the information detailed within the report wording.